## Global_Inputs
Open-FDD ECM Engineering Toolkit — Global Inputs
Shared assumptions used across ECM modules. Yellow cells are agent/human editable; all module calculations remain visible in Excel.
Input | Value | Units | Default / Typical | Basis | API Key
Served floor area | 100000 | ft² | Project specific | User input | global.area_ft2
Electric energy rate | 0.12 | $/kWh | Utility specific | User input | global.electric_rate
Electric demand rate | 15 | $/kW-month | Utility specific | User input | global.demand_rate
Demand billing months | 12 | months/yr | 12 | User input | global.demand_months
Natural gas rate | 1 | $/therm | Utility specific | User input | global.gas_rate
Analysis period | 15 | yr | 10–20 | User input | global.analysis_years
Discount rate | 5% | % | 3–8% | User input | global.discount_rate
Annual utility escalation | 2% | %/yr | 0–3% | User input | global.escalation

## README
Open-FDD ECM Engineering Toolkit
Transparent screening calculations for common HVAC, controls, hydronic, lighting, envelope and plant ECMs. Every engineering equation is visible in workbook cells; the Python API edits the same cells using stable API keys.
Convention | Meaning
Yellow / blue text | Editable human or AI-agent input
Black formulas | Engineering calculation
Green cells | Key output
API Key column | Stable identifier used by Python API
Screening level | Use measured/BAS/vendor data for client-grade estimates
The toolkit intentionally favors measured runtime, airflow, speed, fuel use and equipment performance over invented assumptions. Defaults are starting points, not guarantees.

## ECM_Fan_Schedule
Fan / AHU Runtime Scheduling
Reduces unnecessary fan runtime using measured fan kW and avoided operating hours.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Fan input power | 30 | kW | Measured preferred | INPUT | fan_sched.fan_kw
Baseline annual runtime | 4000 | hr/yr | BAS trend | INPUT | fan_sched.base_hours
Proposed annual runtime | 3000 | hr/yr | Optimized schedule | INPUT | fan_sched.prop_hours
Implementation cost | 5000 | $ | Programming/commissioning | INPUT | fan_sched.cost
CALCULATED OUTPUTS
Annual fan kWh baseline |  | kWh/yr | Visible Excel formula | OUTPUT | fan_sched.base_kwh
Annual fan kWh proposed |  | kWh/yr | Visible Excel formula | OUTPUT | fan_sched.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | fan_sched.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | fan_sched.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | fan_sched.payback

## ECM_Heat_Schedule
Heating Runtime Scheduling
Avoided heating runtime using measured/estimated heating capacity and load factor.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Heating output capacity | 1500 | MBH | Plant/AHU data | INPUT | heat_sched.mbh
Avoided runtime | 300 | hr/yr | BAS schedule evidence | INPUT | heat_sched.hours
Average heating load fraction | 40% | fraction | Trend/calibrated | INPUT | heat_sched.load_frac
Heating efficiency | 82% | % | Boiler/heater | INPUT | heat_sched.eff
Implementation cost | 3000 | $ | Controls | INPUT | heat_sched.cost
CALCULATED OUTPUTS
Delivered heat avoided |  | MMBtu/yr | Visible Excel formula | OUTPUT | heat_sched.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | heat_sched.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | heat_sched.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | heat_sched.payback

## ECM_Cool_Schedule
Cooling Runtime Scheduling
Avoided mechanical-cooling runtime based on tons, kW/ton and load factor.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Cooling capacity | 200 | tons | Chiller/DX capacity | INPUT | cool_sched.tons
Avoided runtime | 250 | hr/yr | BAS schedule evidence | INPUT | cool_sched.hours
Average cooling load fraction | 50% | fraction | Trend/calibrated | INPUT | cool_sched.load_frac
Cooling efficiency | 0.85 | kW/ton | Measured/vendor | INPUT | cool_sched.kw_per_ton
Implementation cost | 3000 | $ | Controls | INPUT | cool_sched.cost
CALCULATED OUTPUTS
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | cool_sched.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | cool_sched.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | cool_sched.payback

## ECM_Unocc_OA_Heat
Unoccupied Outdoor-Air Heating Reduction
Closes/reduces OA during unoccupied warm-up or setback periods; sensible heat only.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Supply airflow | 30000 | cfm | AHU data | INPUT | uoa_h.cfm
Baseline unoccupied OA fraction | 30% | fraction | Existing sequence | INPUT | uoa_h.oa_base
Proposed unoccupied OA fraction | 0% | fraction | Recirculation strategy | INPUT | uoa_h.oa_prop
Indoor/return temperature | 70 | °F | Representative | INPUT | uoa_h.ra_t
Outdoor temperature | 30 | °F | Representative heating bin | INPUT | uoa_h.oa_t
Affected hours | 500 | hr/yr | BAS trend | INPUT | uoa_h.hours
Heating efficiency | 82% | % | Boiler/heater | INPUT | uoa_h.eff
Implementation cost | 2500 | $ | Controls | INPUT | uoa_h.cost
CALCULATED OUTPUTS
Heating load avoided |  | MMBtu/yr | Visible Excel formula | OUTPUT | uoa_h.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | uoa_h.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | uoa_h.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | uoa_h.payback

## ECM_Unocc_OA_Cool
Unoccupied Outdoor-Air Cooling Reduction
Reduces OA latent+sensible cooling during unoccupied operation using moist-air enthalpy difference.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Supply airflow | 30000 | cfm | AHU data | INPUT | uoa_c.cfm
Baseline OA fraction | 30% | fraction | Existing | INPUT | uoa_c.oa_base
Proposed OA fraction | 0% | fraction | Proposed | INPUT | uoa_c.oa_prop
Outdoor-air enthalpy | 38 | Btu/lb | Weather/psychrometric | INPUT | uoa_c.h_oa
Return-air enthalpy | 28 | Btu/lb | BAS/psychrometric | INPUT | uoa_c.h_ra
Affected hours | 400 | hr/yr | BAS trend | INPUT | uoa_c.hours
Cooling COP | 4.5 | COP | Plant | INPUT | uoa_c.cop
Implementation cost | 2500 | $ | Controls | INPUT | uoa_c.cost
CALCULATED OUTPUTS
Cooling load avoided |  | MMBtu/yr | Visible Excel formula | OUTPUT | uoa_c.mmbtu
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | uoa_c.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | uoa_c.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | uoa_c.payback

## ECM_DAT_Reset
Discharge-Air Temperature Reset
Screening estimate for warmer SAT/DAT at low load using measured baseline cooling energy and user-editable efficiency response.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Baseline annual cooling electricity | 250000 | kWh/yr | Utility/model allocation | INPUT | dat.cool_kwh
Average SAT reset | 3 | °F | Weighted annual reset | INPUT | dat.reset_f
Cooling-energy improvement per °F | 1.2% | fraction/°F | Screening/vendor replace | INPUT | dat.gain_per_f
Realization factor | 85% | fraction | Commissioning | INPUT | dat.realization
Implementation cost | 5000 | $ | Controls | INPUT | dat.cost
CALCULATED OUTPUTS
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | dat.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | dat.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | dat.payback

## ECM_Static_Reset
Duct Static-Pressure / Fan-Speed Reset
Measured fan-speed bins are preferred. This simplified module applies fan affinity cube law to weighted baseline/proposed speed.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Design fan input power | 60 | kW | Measured/design | INPUT | spr.fan_kw
Annual runtime | 3500 | hr/yr | BAS | INPUT | spr.hours
Baseline weighted fan speed | 80% | fraction | Trend bins preferred | INPUT | spr.base_speed
Proposed weighted fan speed | 68% | fraction | Post-reset estimate/trend | INPUT | spr.prop_speed
Realization factor | 90% | fraction | Commissioning | INPUT | spr.realization
Implementation cost | 7500 | $ | Controls | INPUT | spr.cost
CALCULATED OUTPUTS
Baseline fan kWh |  | kWh/yr | Visible Excel formula | OUTPUT | spr.base_kwh
Proposed fan kWh |  | kWh/yr | Visible Excel formula | OUTPUT | spr.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | spr.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | spr.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | spr.payback

## ECM_Enthalpy_Econ
Enthalpy Economizer Upgrade
Compares mechanically cooled hours against additional free-cooling hours enabled by enthalpy logic; explicitly caps displacement by observed chiller hours.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Observed chiller run hours | 1200 | hr/yr | BAS | INPUT | econ.run_hours
Additional enthalpy-economizer eligible hours | 220 | hr/yr | Weather/BAS bins | INPUT | econ.eligible_hours
Mechanical-cooling displacement realization | 70% | fraction | Screening | INPUT | econ.realization
Cooling capacity | 180 | tons | Plant/AHU allocation | INPUT | econ.tons
Average load fraction | 55% | fraction | Trend/calibrated | INPUT | econ.load
Chiller efficiency | 0.8 | kW/ton | Measured/vendor | INPUT | econ.kwpt
Implementation cost | 8000 | $ | Sensors/programming | INPUT | econ.cost
CALCULATED OUTPUTS
Displaced chiller hours |  | hr/yr | Visible Excel formula | OUTPUT | econ.displaced_hours
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | econ.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | econ.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | econ.payback

## ECM_Dewpoint_Econ
Dew-Point Economizer Upgrade
Alternative economizer eligibility screening using weather-derived additional suitable cooling hours.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Observed chiller run hours | 1200 | hr/yr | BAS | INPUT | dpe.run_hours
Additional dew-point suitable hours | 180 | hr/yr | Weather bins | INPUT | dpe.hours
Realization factor | 65% | fraction | Screening | INPUT | dpe.realization
Cooling capacity | 180 | tons | Plant | INPUT | dpe.tons
Average load fraction | 55% | fraction | Trend | INPUT | dpe.load
Chiller efficiency | 0.8 | kW/ton | Measured/vendor | INPUT | dpe.kwpt
Implementation cost | 7000 | $ | Controls/sensor | INPUT | dpe.cost
CALCULATED OUTPUTS
Displaced chiller hours |  | hr/yr | Visible Excel formula | OUTPUT | dpe.displaced
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | dpe.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | dpe.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | dpe.payback

## ECM_DCV
Demand-Controlled Ventilation
Reduces excess ventilation at low occupancy. Total cooling uses 4.5×CFM×Δh; heating uses 1.08×CFM×ΔT.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Design OA airflow | 12000 | cfm | Ventilation design | INPUT | dcv.oa_cfm
Average OA reduction | 35% | fraction | Occupancy/trend | INPUT | dcv.reduction
Affected annual hours | 2200 | hr/yr | Schedule | INPUT | dcv.hours
Heating ΔT | 30 | °F | Weighted heating condition | INPUT | dcv.heat_dt
Cooling enthalpy Δh | 8 | Btu/lb | Weighted cooling condition | INPUT | dcv.cool_dh
Heating-hour fraction | 45% | fraction | Weather/schedule | INPUT | dcv.heat_frac
Cooling-hour fraction | 35% | fraction | Weather/schedule | INPUT | dcv.cool_frac
Heating efficiency | 82% | % | Plant | INPUT | dcv.heat_eff
Cooling COP | 4.5 | COP | Plant | INPUT | dcv.cop
Implementation cost | 12000 | $ | CO2 sensors/controls | INPUT | dcv.cost
CALCULATED OUTPUTS
Heating therm saved |  | therm/yr | Visible Excel formula | OUTPUT | dcv.therms
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | dcv.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | dcv.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | dcv.payback

## ECM_Optimal_Start
Adaptive Optimal Start
Replaces fixed prestart with adaptive recovery-rate lead time. Fan savings are directly calculated from avoided prestart runtime.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Baseline prestart lead | 120 | min/day | Existing schedule | INPUT | os.base_min
Average required adaptive lead | 70 | min/day | BAS learned °F/min | INPUT | os.prop_min
Occupied days | 250 | days/yr | Schedule | INPUT | os.days
AHU fan power | 30 | kW | Measured | INPUT | os.fan_kw
Heating/cooling prestart utility savings allowance | 2500 | $/yr | Optional calibrated thermal savings | INPUT | os.thermal_savings
Implementation cost | 6000 | $ | Programming/commissioning | INPUT | os.cost
CALCULATED OUTPUTS
Annual fan hours avoided |  | hr/yr | Visible Excel formula | OUTPUT | os.hours_saved
Fan kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | os.kwh_saved
Annual total $ saved |  | $/yr | Visible Excel formula | OUTPUT | os.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | os.payback

## ECM_Energy_Recovery
Air-to-Air Energy Recovery
Sensible heating recovery plus cooling enthalpy recovery, minus added fan pressure-drop and wheel/pump motor energy.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Outdoor-air airflow | 12000 | cfm | AHU ventilation | INPUT | erv.oa_cfm
Exchange airflow | 12000 | cfm | MIN(OA, exhaust) | INPUT | erv.exchange_cfm
Sensible effectiveness | 70% | fraction | Certified/vendor | INPUT | erv.sens_eff
Heating ΔT | 45 | °F | Weighted condition | INPUT | erv.heat_dt
Heating hours | 1200 | hr/yr | Weather bins | INPUT | erv.heat_hours
Heating efficiency | 82% | % | Plant | INPUT | erv.heat_eff
Cooling enthalpy Δh | 8 | Btu/lb | Weighted condition | INPUT | erv.cool_dh
Cooling hours | 800 | hr/yr | Weather bins | INPUT | erv.cool_hours
Cooling COP | 4.5 | COP | Plant | INPUT | erv.cop
Added total pressure drop | 2 | in.w.g. | Supply+exhaust | INPUT | erv.dp
Fan system efficiency | 60% | fraction | Fan×motor×VFD | INPUT | erv.fan_eff
Wheel/pump motor power | 1.5 | kW | Vendor | INPUT | erv.motor_kw
Implementation cost | 60000 | $ | Installed | INPUT | erv.cost
CALCULATED OUTPUTS
Heating therm saved |  | therm/yr | Visible Excel formula | OUTPUT | erv.therms
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | erv.cool_kwh
Fan/aux kWh penalty |  | kWh/yr | Visible Excel formula | OUTPUT | erv.penalty_kwh
Net annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | erv.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | erv.payback

## ECM_HW_Pump_Control
Hot-Water Pump Runtime Control
Simple runtime reduction for a constant-flow heating-loop pump.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Pump input power | 12 | kW | Measured | INPUT | hwp.kw
Baseline runtime | 5000 | hr/yr | BAS | INPUT | hwp.base_hours
Proposed runtime | 3500 | hr/yr | Schedule/control | INPUT | hwp.prop_hours
Implementation cost | 3000 | $ | Controls | INPUT | hwp.cost
CALCULATED OUTPUTS
Baseline pump kWh |  | kWh/yr | Visible Excel formula | OUTPUT | hwp.base_kwh
Proposed pump kWh |  | kWh/yr | Visible Excel formula | OUTPUT | hwp.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | hwp.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | hwp.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | hwp.payback

## ECM_HW_Reset_Pipe
Hot-Water Reset — Distribution Heat-Loss Reduction
Estimates reduced pipe heat loss from lower average hot-water temperature and credits useful winter heat separately.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Hot-water pipe length | 400 | ft | Field quantity | INPUT | hwrp.length
Existing pipe heat loss | 31 | Btu/hr-ft | Insulation/table | INPUT | hwrp.loss_base
Proposed pipe heat loss | 26 | Btu/hr-ft | Lower water temp/table | INPUT | hwrp.loss_prop
Annual boiler-loop runtime | 4500 | hr/yr | BAS | INPUT | hwrp.hours
Fraction of pipe heat useful to building | 67% | fraction | Engineering judgment | INPUT | hwrp.useful
Boiler efficiency | 82% | % | Plant | INPUT | hwrp.eff
Implementation cost | 4000 | $ | Controls | INPUT | hwrp.cost
CALCULATED OUTPUTS
Net waste heat reduced |  | MMBtu/yr | Visible Excel formula | OUTPUT | hwrp.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | hwrp.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | hwrp.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | hwrp.payback

## ECM_Boiler_Replace
Boiler Efficiency Replacement
Preferred screening method uses measured annual boiler therms and changes only conversion efficiency.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Measured annual boiler gas use | 60000 | therm/yr | Preferred measured input | INPUT | boilrep.therms
Existing thermal efficiency | 80% | % | Measured/nameplate | INPUT | boilrep.old_eff
Proposed thermal efficiency | 94% | % | Vendor | INPUT | boilrep.new_eff
Installed cost | 250000 | $ | Project quote | INPUT | boilrep.cost
CALCULATED OUTPUTS
Delivered useful heat equivalent |  | therm-equivalent/yr | Visible Excel formula | OUTPUT | boilrep.load
Proposed gas use |  | therm/yr | Visible Excel formula | OUTPUT | boilrep.prop_therms
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | boilrep.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | boilrep.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | boilrep.payback

## ECM_Boiler_Reset
Boiler Plant HWST Reset / Condensing Optimization
Incremental plant-efficiency optimization from lower average HWR; use vendor efficiency maps for final analysis.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Annual boiler gas use after any equipment upgrade | 55000 | therm/yr | Measured/calibrated | INPUT | boilrst.base_therms
Baseline seasonal efficiency | 89% | % | Measured/model | INPUT | boilrst.base_eff
Proposed seasonal efficiency | 93% | % | Return-temp efficiency map | INPUT | boilrst.prop_eff
Pump kWh savings | 2000 | kWh/yr | Optional ΔT/flow effect | INPUT | boilrst.pump_kwh
Implementation cost | 12000 | $ | Controls/sensors/Cx | INPUT | boilrst.cost
CALCULATED OUTPUTS
Baseline useful heat |  | therm-equivalent/yr | Visible Excel formula | OUTPUT | boilrst.load
Proposed gas use |  | therm/yr | Visible Excel formula | OUTPUT | boilrst.prop_therms
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | boilrst.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | boilrst.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | boilrst.payback

## ECM_CHW_Reset
Chilled-Water Supply Temperature Reset
Simple low-load CHWS reset. User-editable %/°F correction is a screening proxy; vendor curves are preferred.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Baseline annual chiller energy | 275000 | kWh/yr | Measured/model | INPUT | chwrst.base_kwh
Weighted average CHWS reset | 2.2 | °F | Load-bin result | INPUT | chwrst.reset_f
Efficiency improvement per °F | 1.8% | fraction/°F | Screening proxy | INPUT | chwrst.gain_per_f
Realization factor | 85% | fraction | Controls | INPUT | chwrst.realization
Pump kWh change | 0 | kWh/yr | Positive=savings; negative=penalty | INPUT | chwrst.pump_kwh
Implementation cost | 6000 | $ | Controls/Cx | INPUT | chwrst.cost
CALCULATED OUTPUTS
Chiller kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | chwrst.kwh
Net plant kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | chwrst.net_kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | chwrst.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | chwrst.payback

## ECM_CW_Reset
Cooling-Tower / Condenser-Water Reset
Total-plant screening: colder condenser water may improve chiller efficiency while tower fan energy may rise or fall.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Baseline chiller energy | 272000 | kWh/yr | Measured/model | INPUT | cwrst.ch_kwh
Average condenser-water reduction | 6 | °F | WB+approach bins | INPUT | cwrst.cw_reduction
Chiller improvement per °F | 1.2% | fraction/°F | Screening/vendor replace | INPUT | cwrst.ch_gain
Baseline tower fan energy | 45000 | kWh/yr | Measured/BAS | INPUT | cwrst.tower_base
Proposed tower fan energy | 42000 | kWh/yr | Performance/BAS estimate | INPUT | cwrst.tower_prop
Condenser pump kWh change | 0 | kWh/yr | Positive=savings | INPUT | cwrst.pump_kwh
Implementation cost | 5500 | $ | Controls/sensor/Cx | INPUT | cwrst.cost
CALCULATED OUTPUTS
Chiller kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | cwrst.ch_saved
Tower fan kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | cwrst.tower_saved
Net plant kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | cwrst.net_kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | cwrst.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | cwrst.payback

## ECM_Fan_VFD
Fan VFD Retrofit
Converts constant-speed/damper operation to variable-speed fan control using affinity cube law.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Design fan input power | 40 | kW | Measured/design | INPUT | fvfd.kw
Annual runtime | 3500 | hr/yr | BAS | INPUT | fvfd.hours
Average required airflow fraction | 65% | fraction | Trend/design | INPUT | fvfd.flow_frac
Baseline power fraction | 95% | fraction | Constant-speed/damper | INPUT | fvfd.base_power_frac
VFD efficiency | 97% | fraction | Drive | INPUT | fvfd.vfd_eff
Installed cost | 15000 | $ | Project | INPUT | fvfd.cost
CALCULATED OUTPUTS
Baseline fan kWh |  | kWh/yr | Visible Excel formula | OUTPUT | fvfd.base_kwh
VFD fan kWh |  | kWh/yr | Visible Excel formula | OUTPUT | fvfd.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | fvfd.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | fvfd.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | fvfd.payback

## ECM_Pump_VFD
Pump Variable-Speed / Differential-Pressure Control
Variable-speed pump screening using cube law and measured/estimated average flow fraction.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Design pump input power | 25 | kW | Measured/design | INPUT | pvfd.kw
Annual runtime | 5000 | hr/yr | BAS | INPUT | pvfd.hours
Average required flow fraction | 60% | fraction | Trend/design | INPUT | pvfd.flow_frac
Baseline power fraction | 95% | fraction | Constant speed/throttle | INPUT | pvfd.base_frac
VFD efficiency | 97% | fraction | Drive | INPUT | pvfd.vfd_eff
Installed cost | 12000 | $ | Project | INPUT | pvfd.cost
CALCULATED OUTPUTS
Baseline pump kWh |  | kWh/yr | Visible Excel formula | OUTPUT | pvfd.base_kwh
VFD pump kWh |  | kWh/yr | Visible Excel formula | OUTPUT | pvfd.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | pvfd.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | pvfd.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | pvfd.payback

## ECM_Dirty_Filter
Dirty Filter / Excess Pressure-Drop Correction
Converts avoidable filter pressure drop into fan kW using air horsepower relationship.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Airflow | 30000 | cfm | Measured/design | INPUT | filter.cfm
Avoidable pressure drop | 0.5 | in.w.g. | Measured clean vs dirty | INPUT | filter.dp
Fan efficiency | 60% | fraction | Fan | INPUT | filter.fan_eff
Motor/VFD efficiency | 90% | fraction | Drive train | INPUT | filter.motor_eff
Affected hours | 2500 | hr/yr | BAS/filter condition | INPUT | filter.hours
Implementation cost | 1500 | $ | Maintenance/controls | INPUT | filter.cost
CALCULATED OUTPUTS
Avoidable fan kW |  | kW | Visible Excel formula | OUTPUT | filter.kw
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | filter.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | filter.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | filter.payback

## ECM_Exhaust_Control
Exhaust Fan Scheduling / Control
Avoided exhaust-fan runtime plus optional makeup-air heating/cooling penalty reduction.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Exhaust fan input power | 5 | kW | Measured | INPUT | exh.kw
Avoided runtime | 1800 | hr/yr | Schedule/BAS | INPUT | exh.hours
Exhaust airflow | 5000 | cfm | Measured/design | INPUT | exh.cfm
Makeup heating ΔT | 25 | °F | Weighted | INPUT | exh.heat_dt
Heating-hour fraction | 40% | fraction | Weather | INPUT | exh.heat_frac
Heating efficiency | 82% | % | Plant | INPUT | exh.heat_eff
Implementation cost | 3500 | $ | Controls | INPUT | exh.cost
CALCULATED OUTPUTS
Fan kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | exh.kwh
Heating therm saved |  | therm/yr | Visible Excel formula | OUTPUT | exh.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | exh.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | exh.payback

## ECM_Infiltration
Building Infiltration Reduction
Sensible heating and total/sensible cooling savings from reduced uncontrolled infiltration airflow.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Infiltration reduction | 2000 | cfm | Blower door/estimate | INPUT | inf.cfm
Heating ΔT | 35 | °F | Weighted | INPUT | inf.heat_dt
Heating hours | 1800 | hr/yr | Weather | INPUT | inf.heat_hours
Heating efficiency | 82% | % | Plant | INPUT | inf.heat_eff
Cooling enthalpy Δh | 7 | Btu/lb | Weighted | INPUT | inf.cool_dh
Cooling hours | 800 | hr/yr | Weather | INPUT | inf.cool_hours
Cooling COP | 4.5 | COP | Plant | INPUT | inf.cop
Implementation cost | 30000 | $ | Envelope work | INPUT | inf.cost
CALCULATED OUTPUTS
Heating therm saved |  | therm/yr | Visible Excel formula | OUTPUT | inf.therms
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | inf.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | inf.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | inf.payback

## ECM_Motor_Eff
Premium-Efficiency Motor Replacement
Compares electrical input required for the same shaft load at old vs new motor efficiency.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Motor horsepower | 30 | hp | Nameplate | INPUT | motor.hp
Load fraction | 75% | fraction | Measured/estimate | INPUT | motor.load
Annual runtime | 4000 | hr/yr | BAS | INPUT | motor.hours
Existing motor efficiency | 88% | fraction | Nameplate | INPUT | motor.old_eff
Proposed motor efficiency | 94% | fraction | Premium motor | INPUT | motor.new_eff
Installed incremental cost | 5000 | $ | Project | INPUT | motor.cost
CALCULATED OUTPUTS
Existing kWh |  | kWh/yr | Visible Excel formula | OUTPUT | motor.base_kwh
Proposed kWh |  | kWh/yr | Visible Excel formula | OUTPUT | motor.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | motor.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | motor.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | motor.payback

## ECM_Pipe_Insulation
Pipe Insulation Improvement
Compares linear pipe heat-loss rates before and after insulation.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Pipe length | 500 | ft | Field quantity | INPUT | pipe.length
Existing heat loss | 60 | Btu/hr-ft | Table/calculation | INPUT | pipe.loss_old
Proposed heat loss | 15 | Btu/hr-ft | Table/calculation | INPUT | pipe.loss_new
Annual hot runtime | 5000 | hr/yr | Plant schedule | INPUT | pipe.hours
Fraction heat considered waste | 50% | fraction | Location/season judgment | INPUT | pipe.waste
Heating efficiency | 82% | % | Plant | INPUT | pipe.eff
Installed cost | 18000 | $ | Project | INPUT | pipe.cost
CALCULATED OUTPUTS
Waste heat reduced |  | MMBtu/yr | Visible Excel formula | OUTPUT | pipe.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | pipe.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | pipe.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | pipe.payback

## ECM_Lighting
Lighting Power Retrofit
Simple fixture wattage/quantity/runtime calculation with optional cooling interaction omitted for conservative screening.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Fixture quantity | 500 | count | Survey | INPUT | ltg.qty
Existing watts per fixture | 64 | W | Survey | INPUT | ltg.w_old
Proposed watts per fixture | 32 | W | Design | INPUT | ltg.w_new
Annual operating hours | 3000 | hr/yr | Schedule | INPUT | ltg.hours
Installed cost | 35000 | $ | Project | INPUT | ltg.cost
CALCULATED OUTPUTS
Baseline lighting kWh |  | kWh/yr | Visible Excel formula | OUTPUT | ltg.base_kwh
Proposed lighting kWh |  | kWh/yr | Visible Excel formula | OUTPUT | ltg.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | ltg.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | ltg.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | ltg.payback

## ECM_Lighting_Control
Lighting Scheduling / Occupancy Control
Reduces operating hours of an existing lighting load.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Connected lighting power | 30 | kW | Survey | INPUT | lctl.kw
Baseline runtime | 3500 | hr/yr | Schedule | INPUT | lctl.base_hours
Proposed runtime | 2500 | hr/yr | Occupancy/schedule | INPUT | lctl.prop_hours
Control realization | 90% | fraction | Commissioning | INPUT | lctl.realization
Installed cost | 18000 | $ | Sensors/controls | INPUT | lctl.cost
CALCULATED OUTPUTS
Baseline kWh |  | kWh/yr | Visible Excel formula | OUTPUT | lctl.base_kwh
Proposed kWh |  | kWh/yr | Visible Excel formula | OUTPUT | lctl.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | lctl.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | lctl.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | lctl.payback

## ECM_Humidifier
Humidifier Runtime / Setpoint Optimization
Avoided steam humidification energy from reduced humidifier output or runtime.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Avoided steam rate | 40 | lb/hr | Measured/nameplate | INPUT | hum.lbhr
Avoided runtime | 800 | hr/yr | BAS | INPUT | hum.hours
Steam generation energy | 1100 | Btu/lb | Approx incl. sensible | INPUT | hum.btulb
Boiler efficiency | 80% | % | Plant | INPUT | hum.eff
Implementation cost | 5000 | $ | Controls/repair | INPUT | hum.cost
CALCULATED OUTPUTS
Fuel saved |  | MMBtu/yr | Visible Excel formula | OUTPUT | hum.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | hum.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | hum.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | hum.payback

## ECM_Steam_Leak
Steam Leak Repair
Values avoided steam loss using measured/estimated leak mass flow and steam energy content.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Steam leak rate | 20 | lb/hr | Measured/estimated | INPUT | steam.lbhr
Leak hours | 8760 | hr/yr | Observed | INPUT | steam.hours
Steam energy | 1100 | Btu/lb | Pressure-dependent approx | INPUT | steam.btulb
Boiler efficiency | 80% | % | Plant | INPUT | steam.eff
Repair cost | 8000 | $ | Project | INPUT | steam.cost
CALCULATED OUTPUTS
Fuel saved |  | MMBtu/yr | Visible Excel formula | OUTPUT | steam.mmbtu
Gas saved |  | therm/yr | Visible Excel formula | OUTPUT | steam.therms
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | steam.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | steam.payback

## ECM_Gas_vs_Electric
Gas vs Electric Heating Cost Comparison
Compares annual cost for the same delivered heating load across gas combustion and electric/heat-pump options.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Annual delivered heating load | 5000 | MMBtu/yr | Measured/model | INPUT | fuel.load
Gas heating efficiency | 82% | % | Boiler | INPUT | fuel.gas_eff
Electric heating COP | 3 | COP | Heat pump or 1.0 resistance | INPUT | fuel.cop
Gas-system annual O&M | 5000 | $/yr | Project | INPUT | fuel.gas_om
Electric-system annual O&M | 3000 | $/yr | Project | INPUT | fuel.elec_om
CALCULATED OUTPUTS
Gas annual cost |  | $/yr | Visible Excel formula | OUTPUT | fuel.gas_cost
Electric annual cost |  | $/yr | Visible Excel formula | OUTPUT | fuel.elec_cost
Electric minus gas cost |  | $/yr | Visible Excel formula | OUTPUT | fuel.delta

## ECM_Occ_Sensors
HVAC Occupancy Sensor / Setback Control
Reduces fan and conditioning runtime in intermittently occupied zones/RTUs.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Fan power | 3 | kW | Measured | INPUT | occ.fan_kw
Avoided fan hours | 900 | hr/yr | Occupancy evidence | INPUT | occ.fan_hours
Avoided cooling kWh allowance | 2500 | kWh/yr | Calibrated/optional | INPUT | occ.cool_kwh
Avoided heating therm allowance | 150 | therm/yr | Calibrated/optional | INPUT | occ.heat_therm
Installed cost | 8000 | $ | Sensors/controls | INPUT | occ.cost
CALCULATED OUTPUTS
Fan kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | occ.fan_kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | occ.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | occ.payback

## ECM_Return_Fan
Return Fan Pressure / Fan Synchronization
Reduces return-fan power by lowering unnecessary pressure/speed while maintaining building pressure.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Return fan design power | 25 | kW | Measured/design | INPUT | rfan.kw
Annual runtime | 3500 | hr/yr | BAS | INPUT | rfan.hours
Baseline speed fraction | 80% | fraction | Trend | INPUT | rfan.base_speed
Proposed speed fraction | 68% | fraction | Synced/pressure reset | INPUT | rfan.prop_speed
Implementation cost | 6000 | $ | Controls | INPUT | rfan.cost
CALCULATED OUTPUTS
Baseline kWh |  | kWh/yr | Visible Excel formula | OUTPUT | rfan.base_kwh
Proposed kWh |  | kWh/yr | Visible Excel formula | OUTPUT | rfan.prop_kwh
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | rfan.saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | rfan.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | rfan.payback

## ECM_Unit_Heater_Fan
Unit-Heater / Cabinet-Heater Fan Control
Turns small heating-unit fans off when heat is not required.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Fan power per unit | 0.2 | kW | Measured/nameplate | INPUT | uh.kw
Unit count | 30 | count | Survey | INPUT | uh.count
Avoided runtime | 2500 | hr/yr | Schedule/control | INPUT | uh.hours
Implementation cost | 4500 | $ | Controls | INPUT | uh.cost
CALCULATED OUTPUTS
Annual kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | uh.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | uh.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | uh.payback

## ECM_WHP_Cooling
Water-Source Heat-Pump Cooling Reduction
Screens avoidable simultaneous or unnecessary cooling using measured compressor kW and hours avoided.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Aggregate compressor power | 40 | kW | Measured | INPUT | whp.kw
Avoided cooling runtime | 300 | hr/yr | BAS | INPUT | whp.hours
Realization factor | 85% | fraction | Controls | INPUT | whp.realization
Implementation cost | 6000 | $ | Controls | INPUT | whp.cost
CALCULATED OUTPUTS
Cooling kWh saved |  | kWh/yr | Visible Excel formula | OUTPUT | whp.kwh
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | whp.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | whp.payback

## HVAC_Capacity_Screen
ASHRAE-Style HVAC Capacity Screening
Rule-of-thumb screening only: estimates cooling tons, supply airflow and fan horsepower from floor area.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Floor area | 100000 | ft² | Project | INPUT | cap.area
Square feet per cooling ton | 300 | ft²/ton | Climate/building dependent | INPUT | cap.sf_per_ton
Supply airflow intensity | 1.25 | cfm/ft² | Building dependent | INPUT | cap.cfm_sf
Fan watts per cfm | 0.9 | W/cfm | Screening | INPUT | cap.w_cfm
CALCULATED OUTPUTS
Estimated cooling capacity |  | tons | Visible Excel formula | OUTPUT | cap.tons
Estimated supply airflow |  | cfm | Visible Excel formula | OUTPUT | cap.cfm
Estimated fan input power |  | kW | Visible Excel formula | OUTPUT | cap.fan_kw
Estimated fan horsepower |  | hp | Visible Excel formula | OUTPUT | cap.fan_hp

## Module_Catalog
Open-FDD ECM Module Catalog
Module Sheet | Category | Module Title | Purpose | Primary Output Keys | AI Editable
ECM_Fan_Schedule | Scheduling | Fan / AHU Runtime Scheduling | Reduces unnecessary fan runtime using measured fan kW and avoided operating hours. | fan_sched.base_kwh, fan_sched.prop_kwh, fan_sched.kwh_saved, fan_sched.cost_saved, fan_sched.payback | Yes
ECM_Heat_Schedule | Scheduling | Heating Runtime Scheduling | Avoided heating runtime using measured/estimated heating capacity and load factor. | heat_sched.mmbtu, heat_sched.therms, heat_sched.cost_saved, heat_sched.payback | Yes
ECM_Cool_Schedule | Scheduling | Cooling Runtime Scheduling | Avoided mechanical-cooling runtime based on tons, kW/ton and load factor. | cool_sched.kwh_saved, cool_sched.cost_saved, cool_sched.payback | Yes
ECM_Unocc_OA_Heat | Ventilation | Unoccupied Outdoor-Air Heating Reduction | Closes/reduces OA during unoccupied warm-up or setback periods; sensible heat only. | uoa_h.mmbtu, uoa_h.therms, uoa_h.cost_saved, uoa_h.payback | Yes
ECM_Unocc_OA_Cool | Ventilation | Unoccupied Outdoor-Air Cooling Reduction | Reduces OA latent+sensible cooling during unoccupied operation using moist-air enthalpy difference. | uoa_c.mmbtu, uoa_c.kwh, uoa_c.cost_saved, uoa_c.payback | Yes
ECM_DAT_Reset | Airside Reset | Discharge-Air Temperature Reset | Screening estimate for warmer SAT/DAT at low load using measured baseline cooling energy and user-editable efficiency response. | dat.kwh_saved, dat.cost_saved, dat.payback | Yes
ECM_Static_Reset | Airside Reset | Duct Static-Pressure / Fan-Speed Reset | Measured fan-speed bins are preferred. This simplified module applies fan affinity cube law to weighted baseline/proposed speed. | spr.base_kwh, spr.prop_kwh, spr.kwh_saved, spr.cost_saved, spr.payback | Yes
ECM_Enthalpy_Econ | Economizer | Enthalpy Economizer Upgrade | Compares mechanically cooled hours against additional free-cooling hours enabled by enthalpy logic; explicitly caps displacement by observed chiller hours. | econ.displaced_hours, econ.kwh_saved, econ.cost_saved, econ.payback | Yes
ECM_Dewpoint_Econ | Economizer | Dew-Point Economizer Upgrade | Alternative economizer eligibility screening using weather-derived additional suitable cooling hours. | dpe.displaced, dpe.kwh, dpe.cost_saved, dpe.payback | Yes
ECM_DCV | Ventilation | Demand-Controlled Ventilation | Reduces excess ventilation at low occupancy. Total cooling uses 4.5×CFM×Δh; heating uses 1.08×CFM×ΔT. | dcv.therms, dcv.kwh, dcv.cost_saved, dcv.payback | Yes
ECM_Optimal_Start | Scheduling | Adaptive Optimal Start | Replaces fixed prestart with adaptive recovery-rate lead time. Fan savings are directly calculated from avoided prestart runtime. | os.hours_saved, os.kwh_saved, os.cost_saved, os.payback | Yes
ECM_Energy_Recovery | Ventilation | Air-to-Air Energy Recovery | Sensible heating recovery plus cooling enthalpy recovery, minus added fan pressure-drop and wheel/pump motor energy. | erv.therms, erv.cool_kwh, erv.penalty_kwh, erv.cost_saved, erv.payback | Yes
ECM_HW_Pump_Control | Hydronic | Hot-Water Pump Runtime Control | Simple runtime reduction for a constant-flow heating-loop pump. | hwp.base_kwh, hwp.prop_kwh, hwp.kwh_saved, hwp.cost_saved, hwp.payback | Yes
ECM_HW_Reset_Pipe | Hydronic | Hot-Water Reset — Distribution Heat-Loss Reduction | Estimates reduced pipe heat loss from lower average hot-water temperature and credits useful winter heat separately. | hwrp.mmbtu, hwrp.therms, hwrp.cost_saved, hwrp.payback | Yes
ECM_Boiler_Replace | Boiler | Boiler Efficiency Replacement | Preferred screening method uses measured annual boiler therms and changes only conversion efficiency. | boilrep.load, boilrep.prop_therms, boilrep.saved, boilrep.cost_saved, boilrep.payback | Yes
ECM_Boiler_Reset | Boiler | Boiler Plant HWST Reset / Condensing Optimization | Incremental plant-efficiency optimization from lower average HWR; use vendor efficiency maps for final analysis. | boilrst.load, boilrst.prop_therms, boilrst.saved, boilrst.cost_saved, boilrst.payback | Yes
ECM_CHW_Reset | Chiller | Chilled-Water Supply Temperature Reset | Simple low-load CHWS reset. User-editable %/°F correction is a screening proxy; vendor curves are preferred. | chwrst.kwh, chwrst.net_kwh, chwrst.cost_saved, chwrst.payback | Yes
ECM_CW_Reset | Chiller | Cooling-Tower / Condenser-Water Reset | Total-plant screening: colder condenser water may improve chiller efficiency while tower fan energy may rise or fall. | cwrst.ch_saved, cwrst.tower_saved, cwrst.net_kwh, cwrst.cost_saved, cwrst.payback | Yes
ECM_Fan_VFD | Fans | Fan VFD Retrofit | Converts constant-speed/damper operation to variable-speed fan control using affinity cube law. | fvfd.base_kwh, fvfd.prop_kwh, fvfd.saved, fvfd.cost_saved, fvfd.payback | Yes
ECM_Pump_VFD | Pumps | Pump Variable-Speed / Differential-Pressure Control | Variable-speed pump screening using cube law and measured/estimated average flow fraction. | pvfd.base_kwh, pvfd.prop_kwh, pvfd.saved, pvfd.cost_saved, pvfd.payback | Yes
ECM_Dirty_Filter | Fans | Dirty Filter / Excess Pressure-Drop Correction | Converts avoidable filter pressure drop into fan kW using air horsepower relationship. | filter.kw, filter.kwh, filter.cost_saved, filter.payback | Yes
ECM_Exhaust_Control | Fans | Exhaust Fan Scheduling / Control | Avoided exhaust-fan runtime plus optional makeup-air heating/cooling penalty reduction. | exh.kwh, exh.therms, exh.cost_saved, exh.payback | Yes
ECM_Infiltration | Envelope | Building Infiltration Reduction | Sensible heating and total/sensible cooling savings from reduced uncontrolled infiltration airflow. | inf.therms, inf.kwh, inf.cost_saved, inf.payback | Yes
ECM_Motor_Eff | Motors | Premium-Efficiency Motor Replacement | Compares electrical input required for the same shaft load at old vs new motor efficiency. | motor.base_kwh, motor.prop_kwh, motor.saved, motor.cost_saved, motor.payback | Yes
ECM_Pipe_Insulation | Envelope | Pipe Insulation Improvement | Compares linear pipe heat-loss rates before and after insulation. | pipe.mmbtu, pipe.therms, pipe.cost_saved, pipe.payback | Yes
ECM_Lighting | Lighting | Lighting Power Retrofit | Simple fixture wattage/quantity/runtime calculation with optional cooling interaction omitted for conservative screening. | ltg.base_kwh, ltg.prop_kwh, ltg.saved, ltg.cost_saved, ltg.payback | Yes
ECM_Lighting_Control | Lighting | Lighting Scheduling / Occupancy Control | Reduces operating hours of an existing lighting load. | lctl.base_kwh, lctl.prop_kwh, lctl.saved, lctl.cost_saved, lctl.payback | Yes
ECM_Humidifier | Humidification | Humidifier Runtime / Setpoint Optimization | Avoided steam humidification energy from reduced humidifier output or runtime. | hum.mmbtu, hum.therms, hum.cost_saved, hum.payback | Yes
ECM_Steam_Leak | Steam | Steam Leak Repair | Values avoided steam loss using measured/estimated leak mass flow and steam energy content. | steam.mmbtu, steam.therms, steam.cost_saved, steam.payback | Yes
ECM_Gas_vs_Electric | Fuel | Gas vs Electric Heating Cost Comparison | Compares annual cost for the same delivered heating load across gas combustion and electric/heat-pump options. | fuel.gas_cost, fuel.elec_cost, fuel.delta | Yes
ECM_Occ_Sensors | Scheduling | HVAC Occupancy Sensor / Setback Control | Reduces fan and conditioning runtime in intermittently occupied zones/RTUs. | occ.fan_kwh, occ.cost_saved, occ.payback | Yes
ECM_Return_Fan | Fans | Return Fan Pressure / Fan Synchronization | Reduces return-fan power by lowering unnecessary pressure/speed while maintaining building pressure. | rfan.base_kwh, rfan.prop_kwh, rfan.saved, rfan.cost_saved, rfan.payback | Yes
ECM_Unit_Heater_Fan | Fans | Unit-Heater / Cabinet-Heater Fan Control | Turns small heating-unit fans off when heat is not required. | uh.kwh, uh.cost_saved, uh.payback | Yes
ECM_WHP_Cooling | Heat Pumps | Water-Source Heat-Pump Cooling Reduction | Screens avoidable simultaneous or unnecessary cooling using measured compressor kW and hours avoided. | whp.kwh, whp.cost_saved, whp.payback | Yes
HVAC_Capacity_Screen | Capacity | ASHRAE-Style HVAC Capacity Screening | Rule-of-thumb screening only: estimates cooling tons, supply airflow and fan horsepower from floor area. | cap.tons, cap.cfm, cap.fan_kw, cap.fan_hp | Yes
ECM_Chiller_Lockout | Plant / Cooling | Chiller Outdoor-Air Temperature Lockout | Avoids mechanical cooling below an OAT lockout using plant kW × lockout hours. | lockout.eff_plant_kw, lockout.kwh_saved, lockout.cost_saved, lockout.payback | Yes
ECM_Load_Shed | Demand Response | Demand Response / Load Shed | Peak-period load shed: plant_kw × kW fraction × shed hours. | loadshed.kwh_saved, loadshed.cost_saved, loadshed.payback | Yes
ECM_Schedule_Align | Scheduling | AHU Schedule Align / Opt-Start + OAD 0% Recirc | Industry total = fan cut + cool cut + OAD 0% recirculation; optional fitted FLH stub. | sched.industry_kwh, sched.fitted_kwh, sched.kwh_saved, sched.cost_saved, sched.payback | Yes

## Summary
Open-FDD ECM Engineering Summary
Module | Category | Annual $ Savings | Simple Payback | Status | Notes
Fan / AHU Runtime Scheduling | Scheduling |  |  | Screening | Review project inputs before use
Heating Runtime Scheduling | Scheduling |  |  | Screening | Review project inputs before use
Cooling Runtime Scheduling | Scheduling |  |  | Screening | Review project inputs before use
Unoccupied Outdoor-Air Heating Reduction | Ventilation |  |  | Screening | Review project inputs before use
Unoccupied Outdoor-Air Cooling Reduction | Ventilation |  |  | Screening | Review project inputs before use
Discharge-Air Temperature Reset | Airside Reset |  |  | Screening | Review project inputs before use
Duct Static-Pressure / Fan-Speed Reset | Airside Reset |  |  | Screening | Review project inputs before use
Enthalpy Economizer Upgrade | Economizer |  |  | Screening | Review project inputs before use
Dew-Point Economizer Upgrade | Economizer |  |  | Screening | Review project inputs before use
Demand-Controlled Ventilation | Ventilation |  |  | Screening | Review project inputs before use
Adaptive Optimal Start | Scheduling |  |  | Screening | Review project inputs before use
Air-to-Air Energy Recovery | Ventilation |  |  | Screening | Review project inputs before use
Hot-Water Pump Runtime Control | Hydronic |  |  | Screening | Review project inputs before use
Hot-Water Reset — Distribution Heat-Loss Reduction | Hydronic |  |  | Screening | Review project inputs before use
Boiler Efficiency Replacement | Boiler |  |  | Screening | Review project inputs before use
Boiler Plant HWST Reset / Condensing Optimization | Boiler |  |  | Screening | Review project inputs before use
Chilled-Water Supply Temperature Reset | Chiller |  |  | Screening | Review project inputs before use
Cooling-Tower / Condenser-Water Reset | Chiller |  |  | Screening | Review project inputs before use
Fan VFD Retrofit | Fans |  |  | Screening | Review project inputs before use
Pump Variable-Speed / Differential-Pressure Control | Pumps |  |  | Screening | Review project inputs before use
Dirty Filter / Excess Pressure-Drop Correction | Fans |  |  | Screening | Review project inputs before use
Exhaust Fan Scheduling / Control | Fans |  |  | Screening | Review project inputs before use
Building Infiltration Reduction | Envelope |  |  | Screening | Review project inputs before use
Premium-Efficiency Motor Replacement | Motors |  |  | Screening | Review project inputs before use
Pipe Insulation Improvement | Envelope |  |  | Screening | Review project inputs before use
Lighting Power Retrofit | Lighting |  |  | Screening | Review project inputs before use
Lighting Scheduling / Occupancy Control | Lighting |  |  | Screening | Review project inputs before use
Humidifier Runtime / Setpoint Optimization | Humidification |  |  | Screening | Review project inputs before use
Steam Leak Repair | Steam |  |  | Screening | Review project inputs before use
HVAC Occupancy Sensor / Setback Control | Scheduling |  |  | Screening | Review project inputs before use
Return Fan Pressure / Fan Synchronization | Fans |  |  | Screening | Review project inputs before use
Unit-Heater / Cabinet-Heater Fan Control | Fans |  |  | Screening | Review project inputs before use
Water-Source Heat-Pump Cooling Reduction | Heat Pumps |  |  | Screening | Review project inputs before use

## Sources
Engineering Reference Sources
Topic | Reference | URL | Use
Fan/pump affinity laws | U.S. DOE / fan and pump engineering guidance | https://www.energy.gov/eere/amo/pumping-systems | Cube-law screening for variable-speed equipment
Guideline 36 controls concepts | ASHRAE Guideline 36 | https://www.ashrae.org/technical-resources/bookstore/guideline-36-high-performance-sequences-of-operation-for-hvac-systems | Reset, demand and sequence concepts
Chilled-water plant optimization | LBNL CoolTools Chilled Water Plant Design Guide | https://datacenters.lbl.gov/sites/default/files/EDR_DesignGuidelines_CoolToolsChilledWater.pdf | CHWS/CW reset and total-plant optimization context
Condensing boiler design | ENERGY STAR Commercial Boiler Design Guide | https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Commercial%20Boiler%20Design%20Guide.pdf | Boiler efficiency / return-water context
Moist air / economizer calculations | ASHRAE psychrometric relationships | https://www.ashrae.org/technical-resources/bookstore/psychrometrics | Enthalpy-based ventilation/economizer calculations

## ECM_Chiller_Lockout
Chiller Outdoor-Air Temperature Lockout
Avoids mechanical cooling below an OAT lockout using plant kW × lockout hours (or tons×kW/ton×hours).
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Plant cooling electric demand | 150 | kW | Preferred: metered or tons×kW/ton | INPUT | lockout.plant_kw
Cooling tons (optional) | 230 | tons | Used when plant_kw is 0 | INPUT | lockout.tons
kW per ton | 0.65 | kW/ton | Screening plant efficiency | INPUT | lockout.kw_per_ton
Lockout hours | 600 | h/yr | Hours cooling avoided under OAT lockout | INPUT | lockout.hours
Lockout OAT | 50 | °F | Documentation only | INPUT | lockout.oat_f
Implementation cost | 2500 | $ | Controls | INPUT | lockout.cost
CALCULATED OUTPUTS
Effective plant kW |  | kW | Visible Excel formula | OUTPUT | lockout.eff_plant_kw
Cooling kWh saved |  | kWh/yr | plant_kw × lockout_hours | OUTPUT | lockout.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | lockout.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | lockout.payback

## ECM_Load_Shed
Demand Response / Load Shed
Peak-period load shed screening: plant_kw × kW fraction × shed hours (not annual FLH greenwash).
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Plant cooling electric demand | 150 | kW | tons × kW/ton or metered | INPUT | loadshed.plant_kw
Load-shed kW fraction | 0.13 | fraction | July DR pair / screening | INPUT | loadshed.kw_fraction
Load-shed hours | 2 | h/event | DR window length | INPUT | loadshed.hours
DAT raise during shed | 3 | °F | Documentation | INPUT | loadshed.delta_f
Implementation cost | 1500 | $ | Controls / DR enrollment | INPUT | loadshed.cost
CALCULATED OUTPUTS
Event kWh saved |  | kWh/event | plant_kw × fraction × hours | OUTPUT | loadshed.kwh_saved
Annual $ saved (1 event/yr default) |  | $/yr | Edit for event count | OUTPUT | loadshed.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | loadshed.payback

## ECM_Schedule_Align
AHU Schedule Align / Opt-Start + OAD 0% Recirc
Industry total = fan cut + cool cut + OAD 0% recirculation. Fitted stub uses (fan_kw+0.15×plant)×hours_saved when FLH reverse-solved.
Input / Output | Value | Units | Basis / Formula | Type | API Key
INPUTS
Fan electric demand | 40 | kW | Metered / eio | INPUT | sched.fan_kw
Plant cooling electric demand | 150 | kW | tons × kW/ton | INPUT | sched.plant_kw
Fitted hours saved (optional) | 1000 | h/yr | FITTED_FROM_EPLUS when reverse-solved | INPUT | sched.hours_saved
Implementation cost | 8000 | $ | Controls / opt-start | INPUT | sched.cost
Current weekly AHU hours | 71.25 | h/wk | Industry screening | INPUT | sched.current_weekly_h
Future weekly AHU hours | 49.5 | h/wk | Opt-start target before pad | INPUT | sched.future_weekly_h
Override pad | 1.1 | fraction | Industry 10% allowance | INPUT | sched.override_pad
Warmup/cooldown/unocc hours | 450 | h/yr | OAD 0% opportunity hours | INPUT | sched.warmup_cooldown_h
Baseline coil tons | 180 | tons | Industry cool cut | INPUT | sched.tons_base
Cooling-bin hours | 1800 | h/yr | Industry | INPUT | sched.cool_bin_hours
kW per ton | 0.65 | kW/ton | Industry | INPUT | sched.kw_per_ton
Annual fan run hours | 3000 | h/yr | Before opt-start | INPUT | sched.fan_run_hours
OAD tons delta (MA−full recirc) | 15 | tons | Industry OAD 0% | INPUT | sched.oad_tons_delta
CALCULATED OUTPUTS
Hours reduction fraction |  | fraction | 1 − future_pad/current | OUTPUT | sched.hours_reduction_frac
SCHED_FAN kWh |  | kWh/yr | fan × run hours × reduction | OUTPUT | sched.fan_kwh
SCHED_COOL kWh |  | kWh/yr | coil × hours × reduction | OUTPUT | sched.cool_kwh
OAD_RECIRC kWh |  | kWh/yr | OAD 0% warmup/cooldown | OUTPUT | sched.oad_kwh
Industry SCHED_ALIGN kWh |  | kWh/yr | fan + cool + OAD | OUTPUT | sched.industry_kwh
Fitted stub kWh |  | kWh/yr | (fan+0.15×plant)×fitted hours | OUTPUT | sched.fitted_kwh
Primary kWh saved (industry) |  | kWh/yr | Prefer industry over fitted stub | OUTPUT | sched.kwh_saved
Annual $ saved |  | $/yr | Visible Excel formula | OUTPUT | sched.cost_saved
Simple payback |  | yr | Visible Excel formula | OUTPUT | sched.payback