## Cover
Liberty Building 100 — Full-parity ECM screening
Twin geo_b100_dual_ahu_shape_ops11 · dual-AHU (VAV Sys 1+2, 6×2 zones) · G14 PASS · vs_baseline only
Sheets
Cover · Twin_Calibrate · Architecture · Schedules · Inputs · Industry_Screening · Per_AHU · Measures · Formula_Trace · Matchup · Documentation
Honesty
Screening ≠ M&V. Dual AirLoopHVAC with 50/50 area share. IMPORTANT: most measure sheet_kWh use Excel formulas whose FLH Inputs were FITTED FROM EnergyPlus (hours = eplus_kWh / plant factor) — status=FITTED, not a blind independent BALLPARK. See Formula_Trace. Negative E+ savings = FAIL_SIGN. Package gaps: reports/BUG_REPORT.md.

## Twin_Calibrate
Twin calibration vs utility bills (G14)
Run geo_b100_dual_ahu_shape_ops11 · elec NMBE -2.63% CV 14.77% · gas NMBE -0.19% CV 14.98% · g14_pass=True
Gate
fuel | NMBE_% | CVRMSE_% | pass_¦NMBE¦≤5 | pass_CV≤15 | pass
elec | -2.629 | 14.77 | TRUE | TRUE | TRUE
gas | -0.193 | 14.976 | TRUE | TRUE | TRUE
Monthly modeled vs actual (±%)
month | bill_kwh | sim_kwh | elec_delta_pct | bill_therms | sim_therms | gas_delta_pct
2024-12 | 85928.5 | 86626.6 | 0.8 | 5956.5 | 7097.8 | 19.2
2025-01 | 103446 | 88115.3 | -14.8 | 8540.7 | 9723 | 13.8
2025-02 | 104909 | 83904.7 | -20 | 11715 | 10762.4 | -8.1
2025-03 | 102966.5 | 118696.1 | 15.3 | 8158.1 | 7034.9 | -13.8
2025-04 | 100089.5 | 123688.9 | 23.6 | 6226.1 | 5656.8 | -9.1
2025-05 | 116623.5 | 142731.1 | 22.4 | 3676.2 | 3988.2 | 8.5
2025-06 | 127603 | 149463.4 | 17.1 | 2634 | 2308.6 | -12.4
2025-07 | 170033.5 | 161823.7 | -4.8 | 1141.7 | 1199.6 | 5.1
2025-08 | 174594 | 186235 | 6.7 | 807.8 | 852.6 | 5.5
2025-09 | 127799 | 140712.7 | 10.1 | 2059.5 | 2111.9 | 2.5
2025-10 | 140577.5 | 133842.9 | -4.8 | 1517.1 | 1450 | -4.4
2025-11 | 109879 | 87112.9 | -20.7 | 4412.4 | 4769 | 8.1
Building massing (IDF footprint)
Note: 2D footprint from Floor surfaces. Studio Twin 3D Plotly massing is not embedded (kaleido not in vibe20 tip) — see BUG_REPORT ENH-XLSX-MASSING-3D.

## Architecture
Architectural / systems summary (answers + IDF)
Not a full OpenStudio-style shell form — fields populated from Twin answers.json + parsed IDF geometry. Gaps marked NEEDS_ENH.
field | value | source
Name | Liberty Building 100 (Detroit MI) — 6fl curtain wall WC chillers | answers
Building Type | office | answers
City / climate proxy | detroit | answers
Area (ft²) | 140000 | answers
Floors | 6 | answers
Floor-to-floor (ft) | 13 | answers
Aspect (bbox dx/dy) | 1.5 | IDF geometry
Footprint dx×dy (ft) | 187.1 × 124.7 | IDF geometry
Stack height dz (ft) | 78 | IDF geometry
IDF zones | 12 | IDF geometry
Zone names | Floor_1_AHU1, Floor_1_AHU2, Floor_2_AHU1, Floor_2_AHU2, Floor_3_AHU1, Floor_3_AHU2, Floor_4_AHU1, Floor_4_AHU2, Floor_5_AHU1, Floor_5_AHU2, Floor_6_AHU1, Floor_6_AHU2 | IDF geometry
WWR answers | 0.6 | answers
WWR from IDF surfaces | 0.543 | IDF geometry
Wall area m² | 6326.52 | IDF geometry
Window area m² | 3434.46 | IDF geometry
Roof area m² | 13006.42 | IDF geometry
Fenestration count | 36 | IDF geometry
Heating fuel | gas | answers
Air-side system | vav_reheat | answers
Cooling / plant | water_cooled_chiller | answers
Air loops | VAV Sys 1 + VAV Sys 2 (dual-AHU) | IDF geometry
Perimeter zone depth | NEEDS_ENH (not stamped on answers) | gap — see BUG_REPORT
Roof / wall / glazing type labels | NEEDS_ENH (IDF constructions exist; no friendly labels) | gap — see BUG_REPORT
DOAS | None / NEEDS_ENH | gap — see BUG_REPORT
DHW | NEEDS_ENH | gap — see BUG_REPORT
Annual water gal/ft² | NEEDS_ENH | gap — see BUG_REPORT
Notes | Site-scale DOE Large Office adapted: 140k conditioned, 6 floors, WWR 0.60 pure-glass proxy, water-cooled chillers + cooling tower. Atrium/3-story Google claims deferred. Bills = area-weighted half shared elec + B100 gas. ¦ dial R4: lights 4.5 W/m2, equip 4.2 W/m2, infil×1.40 via EnergyPlus MCP | answers

## Schedules
As-operated schedules (IDF excerpts)
Raw Schedule:Compact from Twin IDF — not an OpenStudio weekday grid. Friendly ASHRAE grid export = ENH-XLSX-SCHEDULE-GRID (BUG_REPORT).
AHU fan availability (ops-odd months)
Schedule:Compact,
FanAvailSched, On/Off,
Through: 2/28,
For: Weekdays SummerDesignDay,
Until: 10:00, 0.0, Until: 20:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 10:00, 0.0, Until: 18:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 6/30,
For: Weekdays SummerDesignDay,
Until: 9:00, 0.0, Until: 19:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 9:00, 0.0, Until: 17:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 7/31,
For: Weekdays SummerDesignDay,
Until: 9:00, 0.0, Until: 23:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 9:00, 0.0, Until: 20:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 8/31,
For: AllDays,
Until: 24:00, 1.0,
Through: 9/30,
For: Weekdays SummerDesignDay,
Until: 9:00, 0.0, Until: 23:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 9:00, 0.0, Until: 20:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 10/31,
For: Weekdays SummerDesignDay,
Until: 7:00, 0.0, Until: 23:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 8:00, 0.0, Until: 22:00, 1.0, Until: 24:00, 0.
… truncated …
Minimum outdoor air fraction
Schedule:Compact,
Min OA Sched, Fraction,
Through: 1/31,
For: AllDays,
Until: 24:00, 0.0,
Through: 2/28,
For: Weekdays SummerDesignDay,
Until: 5:00, 0.0, Until: 23:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 6:00, 0.0, Until: 20:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.3,
Through: 6/30,
For: Weekdays SummerDesignDay,
Until: 10:00, 0.0, Until: 18:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 10:00, 0.0, Until: 16:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 7/31,
For: Weekdays SummerDesignDay,
Until: 6:00, 0.0, Until: 22:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 6:00, 0.0, Until: 18:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 8/31,
For: AllDays,
Until: 24:00, 0.0,
Through: 9/30,
For: Weekdays SummerDesignDay,
Until: 6:00, 0.0, Until: 22:00, 1.0, Until: 24:00, 0.0,
For: Saturday,
Until: 6:00, 0.0, Until: 18:00, 1.0, Until: 24:00, 0.0,
For: AllOtherDays,
Until: 24:00, 0.0,
Through: 10/31,
For: Weekdays SummerDesignDay,
Until: 7:00, 0.0, Until: 23:00, 0.15, Until: 24:00, 0.0,
For: Saturday,
… truncated …
HW plant lockout / daytime (if present)
Schedule:Compact,
HW AugOct Plant Avail, On/Off,
Through: 7/31,
For: AllDays,
Until: 24:00, 1,
Through: 8/31,
For: Weekdays SummerDesignDay,
Until: 8:00, 0, Until: 18:00, 1, Until: 24:00, 0,
For: Saturday,
Until: 9:00, 0, Until: 16:00, 1, Until: 24:00, 0,
For: AllOtherDays,
Until: 24:00, 0,
Through: 9/30,
For: AllDays,
Until: 24:00, 1,
Through: 10/31,
For: Weekdays SummerDesignDay,
Until: 9:00, 0, Until: 15:00, 1, Until: 24:00, 0,
For: Saturday,
Until: 10:00, 0, Until: 13:00, 1, Until: 24:00, 0,
For: AllOtherDays,
Until: 24:00, 0,
Through: 12/31,
For: AllDays,
Until: 24:00, 1;
Cooling setpoint schedule
Schedule:Compact,
Htg-SetP-Sch, Temperature,
Through: 12/31,
For: Weekdays SummerDesignDay,
Until: 6:00, 15.6, Until: 22:00, 21.0, Until: 24:00, 15.6,
For: Saturday,
Until: 6:00, 15.6, Until: 18:00, 21.0, Until: 24:00, 15.6,
For: AllOtherDays, Until: 24:00, 15.6;
Heating setpoint schedule
Schedule:Compact,
Clg-SetP-Sch, Temperature,
Through: 12/31,
For: Weekdays SummerDesignDay,
Until: 6:00, 30.0, Until: 22:00, 24.0, Until: 24:00, 30.0,
For: Saturday,
Until: 6:00, 30.0, Until: 18:00, 24.0, Until: 24:00, 30.0,
For: AllOtherDays, Until: 24:00, 30.0;
Thermostat setpoints (OpenStudio-style occupied/unoccupied grid)
NEEDS_ENH — Twin uses scheduled DualSetpoint; no separate occ/unocc simple thermostats stamped.

## Inputs
Building Inputs (named ranges for Measures formulas)
Yellow FLH rows are reverse-solved from E+ so formula × hours ≈ eplus_kWh. That is FITTED, not an independent engineering estimate. See Formula_Trace / BUG-ECM-018.
name | value | provenance | assumption_note
cooling_tons | 255.27 | VALUE | eio MAIN CHILLER (matched book)
fan_hp | 52.4 | VALUE | eio fan HP (matched book)
kw_per_ton | 0.65 | VALUE | screening plant efficiency
plant_kw |  | FORMULA | tons×kW/ton
fan_kw |  | FORMULA | HP×0.746
elec_usd_per_kwh | 0.14 | VALUE | Inputs rate
lockout_hours | 612.2058 | FITTED_FROM_EPLUS | eplus_lockout / plant_kw
sched_hours_saved | 1163.659 | FITTED_FROM_EPLUS | eplus_sched / (fan+0.15*plant)
fan_hours | 3516.6684 | FITTED_FROM_EPLUS | eplus_dsp / fan affinity factor
sat_hours | 9202.8004 | FITTED_FROM_EPLUS | ¦eplus_sat¦ / (plant*0.08)
sat_sign | 1 | VALUE | +1 or −1 from cascade sign
econ_hours | 55.7634 | FITTED_FROM_EPLUS | eplus_econ / (plant*0.35)
chw_reset_hours | 4879.4389 | FITTED_FROM_EPLUS | eplus_chw / (plant*0.06)
standby_hours | 133.6791 | FITTED_FROM_EPLUS | eplus_occ / (0.45*fan+0.12*plant)
erv_hours | 1499.0412 | FITTED_FROM_EPLUS | eplus_erv / (plant*0.12)
loadshed_hours | 2 | SCREENING_ASSUMPTION | July DR window length
loadshed_kw_fraction | 0.13 | SCREENING_ASSUMPTION | July MCP fraction — not fitted

## Industry_Screening
Industry-method screening (independent — not fitted to EnergyPlus)
Formulas mirror anonymized ESCO VAV/chiller calculators (DAT, DSP, enthalpy econ, CHW, opt-start fan+cooling, OAD 0% unocc/warmup = full recirculation). HP-DOAS books excluded. See reports/ecm_industry_method_gap.md. Yellow Inputs = FITTED audit only.
Shared plant / airside
name | value | provenance | note
supply_cfm |  | FORMULA | ≈400 cfm/ton screening; edit cfm_per_ton
cfm_per_ton | 400 | INDUSTRY_DEFAULT | ESCO books use metered Unit CFM when known
oa_frac | 0.2 | INDUSTRY_DEFAULT | OA/SA fraction for mixed-air enthalpy
h_ra | 28.3 | INDUSTRY_DEFAULT | Return enthalpy Btu/lb (typical 75°F / 50–60% RH)
h_oa_cool | 30 | INDUSTRY_DEFAULT | Season-average OA enthalpy in cooling bins (edit for climate)
h_sat_base | 23.2 | INDUSTRY_DEFAULT | Baseline DAT enthalpy ~55°F supply
h_sat_reset | 25.5 | INDUSTRY_DEFAULT | Reset DAT enthalpy ~58–60°F (raise SAT)
dat_load_factor | 0.7 | INDUSTRY_DEFAULT | Part-load factor on coil (industry M column)
cool_bin_hours | 1800 | INDUSTRY_DEFAULT | Occupied cooling-bin hours (proxy for full NOAA table)
dsp_avg_speed | 0.75 | INDUSTRY_DEFAULT | Baseline average fan speed fraction
dsp_pressure_factor | 0.7 | INDUSTRY_DEFAULT | Industry static reset pressure ratio (~0.7)
fan_run_hours | 3000 | INDUSTRY_DEFAULT | Annual fan run hours before opt-start (not E+-fitted)
chw_kwpt_improve | 0.08 | INDUSTRY_DEFAULT | ΔkW/ton from CHW reset (screening)
chw_equiv_full_load_h | 1200 | INDUSTRY_DEFAULT | Equivalent full-load chiller hours
econ_oa_good_hours | 800 | INDUSTRY_DEFAULT | Hours OA enthalpy < return (enthalpy econ window)
econ_oa_cfm_frac | 0.35 | INDUSTRY_DEFAULT | Fraction of supply that can be free-cooled when OA good
sched_current_weekly_h | 71.25 | INDUSTRY_DEFAULT | Current AHU weekly hours (e.g. 2.25+8+4)×5)
sched_future_weekly_h | 49.5 | INDUSTRY_DEFAULT | Future opt-start weekly hours before override pad
sched_override_pad | 1.1 | INDUSTRY_DEFAULT | Industry 10% allowance on future hours (overrides)
warmup_cooldown_h | 450 | INDUSTRY_DEFAULT | Annual warmup/cooldown/unocc hours still needing air (OAD 0%)
DAT / SAT reset (industry psychrometric form)
h_ma |  | mixed-air enthalpy
tons_base
tons_reset
DAT_kwh |  | must be ≥0 if reset raises SAT (industry)
Duct static pressure reset (industry affinity)
dsp_red_speed |  | speed / √(1/0.7) ≡ speed×√0.7
DSP_kwh
CHW OA reset (simplified industry ΔkW/ton)
CHW_kwh |  | full bin×load%×ΔkW/ton in ESCO books — this is annual equiv
Enthalpy economizer (simplified industry window)
ECON_kwh |  | when OA enthalpy helpful vs return — not plant×0.35×fitted
AHU schedule / opt-start + OAD 0% warmup (industry VV Scheduling + OAD)
sched_future_weekly_pad |  | future hours × 1.1 override pad (ESCO)
hours_reduction_frac |  | minimize run hours: 1 − future/current
SCHED_FAN_kwh |  | VV Scheduling_Fan: fan_kW × annual hours × reduction
SCHED_COOL_kwh |  | VV Scheduling_Cooling: coil energy × same hour cut
tons_ma_vent |  | coil tons with min-OA mixed air
tons_full_recirc |  | coil tons at OA=0% (100% return / full recirculation)
OAD_RECIRC_kwh |  | VV OAD 0% Unocc: warmup/cooldown/unocc → full recirculation (not min OA)
SCHED_ALIGN_kwh |  | ECM-AHU-SCHED-ALIGN industry total (fan + cool cut + OAD 0%)
Why E+ SAT is negative on this Twin
Cascade patch sets flat 14°C (57°F) year-round, overriding seasonal Dump_AHU DAT (winter dump ~28°C). That adds winter cooling kWh. Industry DAT reset raises SAT under low load — it does not flatten over dump months. Use tools/patch_sat_reset_dual_ahu.py. SCHED_ALIGN uses industry opt-start + OAD 0% recirculation — not fitted FLH.

## Per_AHU
Per-AHU allocation (engineer view)
Twin E+ SoT = VAV Sys 1 + VAV Sys 2. Building vs_baseline split 50% / 50% by equal zone area.
ahu_id | twin_airloop | share_of_twin | plant_kw | fan_kw | oa_cfm_screen | assumption_note
AHU_1 | VAV Sys 1 | 0.5 | 82.96 | 19.55 | autosize OA | Floor_*_AHU1
AHU_2 | VAV Sys 2 | 0.5 | 82.96 | 19.55 | autosize OA | Floor_*_AHU2
measure_id | AHU_1_kwh | AHU_2_kwh | building_kwh | excel_formula
ECM-ECON-REPAIR | 1619.2 | 1619.2 | 3238.4 | 0.50/0.50 × (=plant_kw*0.35*econ_hours)
ECM-CHILLER-LOCKOUT | 50790.3 | 50790.3 | 101580.6 | 0.50/0.50 × (=plant_kw*lockout_hours)
ECM-AHU-SCHED-ALIGN | 37225 | 37225 | 74450 | 0.50/0.50 × (=(fan_kw+plant_kw*0.15)*sched_hours_saved)
ECM-DSP-RESET | 14587.5 | 14587.5 | 29175 | 0.50/0.50 × (=fan_kw*(1-0.85^3)*0.55*fan_hours)
ECM-SAT-RESET | 61079.2 | 61079.2 | 122158.3 | 0.50/0.50 × (=plant_kw*0.08*sat_hours*sat_sign)
ECM-CHW-RESET | 24288.7 | 24288.7 | 48577.4 | 0.50/0.50 × (=plant_kw*0.06*chw_reset_hours)
ECM-OCC-STANDBY-DCV | 2506.6 | 2506.6 | 5013.2 | 0.50/0.50 × (=(fan_kw*0.45+plant_kw*0.12)*standby_hours)
ECM-AHU-ERV | 14923.8 | 14923.8 | 29847.5 | 0.50/0.50 × (=plant_kw*0.12*erv_hours)
ECM-LOAD-SHED-DR | 34.5 | 34.5 | 69 | 0.50/0.50 × (=plant_kw*loadshed_kw_fraction*loadshed_hours)

## Measures
Measure roster (building total)
Industry screening = 2nd set of eyes (ESCO methods; E+ must not be way off). pct_diff_* = (sheet − eplus) / max(¦eplus¦,1). SCHED_ALIGN = minimize run hours (fan+cool) + OAD 0% warmup/cooldown full recirculation. SAT eplus uses fixed dual-AHU patch when present (BUG-ECM-019).
measure_id | name | phase | eplus_source | fitted_sheet_kwh | eplus_kwh | pct_diff_fitted_vs_eplus | industry_screen_kwh | pct_diff_industry_vs_eplus | annual_usd | status | excel_formula_fitted | hours_provenance | industry_formula
ECM-ECON-REPAIR | Enthalpy economizer | 1 | MCP prototype |  | 3238.4 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS
ECM-CHILLER-LOCKOUT | Chiller OAT lockout | 1 | cascade |  | 101580.56 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS | n/a — keep fitted or add bin sheet
ECM-AHU-SCHED-ALIGN | AHU schedule / opt-start + OAD 0% recirc | 1 | cascade |  | 74450 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS
ECM-DSP-RESET | G36 duct static reset | 2 | cascade |  | 29175 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS
ECM-SAT-RESET | SAT / DAT reset | 2 | fixed_patch_dual_ahu |  | 122158.34 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS
ECM-CHW-RESET | CHW OA reset | 2 | MCP prototype |  | 48577.4 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS
ECM-OCC-STANDBY-DCV | Occ/standby (Floor_6 proxy) | 2 | MCP prototype |  | 5013.2 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS | n/a — keep fitted or add bin sheet
ECM-AHU-ERV | AHU air-side ERV (toilet/relief) | 2 | MCP prototype ERV |  | 29847.5 |  |  |  |  | FITTED |  | FITTED_FROM_EPLUS | n/a — keep fitted or add bin sheet
ECM-LOAD-SHED-DR | Load shed +3°F × 2 h | 2 | July MCP pair |  | 69 |  |  |  |  | BALLPARK |  | SCREENING_ASSUMPTION | n/a — keep fitted or add bin sheet

## Formula_Trace
Formula traceability + % diff (2nd set of eyes)
Industry screening is the independent check — E+ should not be way off from it. Large ¦pct_diff_industry_vs_eplus¦ => investigate IDF/patch (SAT flat-14C / dual-AHU). fitted %~0 by construction (BUG-ECM-018). Patch: tools/patch_sat_reset_dual_ahu.py.
measure_id | excel_formula | hours_provenance | how_hours_were_set | fitted_kwh | eplus_kwh | pct_fitted | status | industry_kwh | pct_industry
ECM-ECON-REPAIR |  | FITTED_FROM_EPLUS | econ_hours = eplus_kWh / (plant_kw*0.35) | 3238.4 | 3238.4 | 0% | FITTED | 35541.2 | 997.5%
ECM-CHILLER-LOCKOUT |  | FITTED_FROM_EPLUS | lockout_hours = eplus_kWh / plant_kw | 101580.6 | 101580.56 | 0% | FITTED
ECM-AHU-SCHED-ALIGN |  | FITTED_FROM_EPLUS | fitted FLH audit; industry SCHED_ALIGN = fan cut + cool cut + OAD 0% full recirculation | 74450 | 74450 | 0% | FITTED | 70542.1 | -5.25%
ECM-DSP-RESET |  | FITTED_FROM_EPLUS | fan_hours = eplus / (fan_kw*(1-0.85^3)*0.55) | 29175 | 29175 | 0% | FITTED | 20498.9 | -29.74%
ECM-SAT-RESET |  | FITTED_FROM_EPLUS | prefer ecm_sat_reset_fixed kWh; industry DAT_kwh = psychrometric raise | 122158.3 | 122158.34 | -0% | FITTED | 72127.8 | -40.96%
ECM-CHW-RESET |  | FITTED_FROM_EPLUS | chw_reset_hours = eplus / (plant_kw*0.06) | 48577.4 | 48577.4 | 0% | FITTED | 24505.9 | -49.55%
ECM-OCC-STANDBY-DCV |  | FITTED_FROM_EPLUS | standby_hours = eplus / (fan_kw*0.45+plant_kw*0.12) | 5013.2 | 5013.2 | 0% | FITTED
ECM-AHU-ERV |  | FITTED_FROM_EPLUS | erv_hours = eplus / (plant_kw*0.12) | 29847.5 | 29847.5 | 0% | FITTED
ECM-LOAD-SHED-DR |  | SCREENING_ASSUMPTION | 2 h × 0.13 fraction — NOT fitted to July MCP pair | 43.1 | 69 | -37.48% | BALLPARK
Independent check (not fitted)
ECM-LOAD-SHED-DR: fixed 2h x 0.13 vs July MCP (~69 kWh).
SAT IDF: docker exec vibe20 python /data/tools/patch_sat_reset_dual_ahu.py (BUG-ECM-019).

## Matchup
Calendar vs FLH + industry 2nd-eyes % gap
layer | value | note
chiller_tons_eio | 255.27 | from matched book (re-match dual eio = ENH)
fan_hp_eio | 52.4 | from matched book
fitted_flh | YES for 8/9 measures | fitted %~0 by construction
industry_screening | DAT 72128 / DSP 20499 / CHW 24506 / ECON 35541 / SCHED 70542 kWh | 2nd eyes ESCO: DAT+DSP+CHW+ECON+opt-start/OAD0% — reports/ecm_industry_method_gap.md
sat_idf_patch | tools/patch_sat_reset_dual_ahu.py | BUG-ECM-019 — replace tip flat-14C Sys1-only
finding |  | matched book

## Documentation
Documentation
Rebuild: docker exec vibe20 python /data/tools/build_full_parity_ecm_workbook_v2.py
Twin CURRENT: geo_b100_dual_ahu_shape_ops11 (dual-AHU full G14)
Savings: baseline - single-measure Twin (vs_baseline). Never add rows as a package.
2nd eyes: Industry_Screening + pct_diff_industry_vs_eplus. SAT fix: tools/patch_sat_reset_dual_ahu.py. BUG_REPORT A2/A2b + BUG-ECM-018/019.
Enhancement backlog: reports/BUG_REPORT.md