## INFO
uesgraphs Parameter Template
Version: 3.0
This Excel template provides parameters for generating pandapipes district heating/cooling network models.
Fill in the parameters in each sheet, then use this file with uesgraphs.create_model().
Sheet Overview:
Sheet Name | Purpose | Required?
Simulation | General simulation settings (solver, times, medium) | YES
Demands | Common parameters for all demand/substation nodes | YES
Supply | Common parameters for all supply nodes | YES
Pipes | Common parameters for all pipe edges | YES
Individual_Parameters | Optional: Override parameters for specific nodes/edges | NO (future)
Important Notes:
1. UNITS: All values must use SI units (K for temperature, Pa for pressure, W for power, etc.)
2. INDIVIDUAL PARAMETERS: Parameters like pipe diameter, length, individual loads MUST be in uesgraph!
3. PRIORITY: Individual graph parameters > Excel common parameters
Quick Start:
1. Adjust parameter values as needed for your network
2. Ensure your uesgraph has all individual parameters (diameter, length, coordinates, etc.)
3. Run: uesgraphs.create_model(graph, excel_path="this_file.xlsx")
For more information, see: https://github.com/RWTH-EBC/uesgraphs

## Simulation
Parameter | Value | Unit | Description
simulation_name | MyProject | - | Name of the simulation
start_time | 0 | s | Simulation start time
stop_time | 31536000 | s | Simulation stop time (86400s = 24h)
timestep | 3600 | s
mode | static | - | Mode for dynamic or static simulation must be set either to „dynamic“ or to „static“ or „transient“ for full pandapipes simulation
save_params_to_csv | TRUE | bool | If TRUE, save parameters to CSV file next to modelica folder
ground_depth | 1.0 m | string | Ground depth for embedded pipes
temp_dT_dhw | 35 | K | Only for DHW calc, temperature difference between freshwater and average DHW outlet temperature
mean_drawoff_vol_per_day | 40 | L/day | Only for DHW calc, Mean drawoff volume per person for a day

## Demands
Parameter | Value | Unit | Description
dT_Network | 17 | K | Temperature difference in network
cp_default | 4180 | J/(kg·K) | Specific heat capacity (default: 4180 for water)
TReturn | 302.15 | K | Default return temperature

## Supply
Parameter | Value | Unit | Description
pIn | 230000 | Pa | Fixed suppy pressure
dpFlow | 30000 | Pa | Fixed pressure lift in circulation pump
pReturn | 200000 | Pa | Default return pressure based on pIn and dpFlow
TIn | 319.15 | K | Fixed supply temperature
TReturn | 302.15 | K | Default return temperature

## Pipes
Parameter | Value | Unit | Description
dIns | 0.1 | m | Thickness of pipe insulation (used to compute thermal resistance R)
kIns | 0.026 | W/(m·K) | Heat conductivity of pipe insulation (used to compute R)
roughness | 0 | mm | Average height of surface asperities
ground_depth | 1 | m | Depth at which ground temperature is extracted (external file must be provided)
sections | 5 | - | Default value of 5 sections for the calculation of values within the pipe

## Individual_Parameters
OPTIONAL FEATURE - Individual Node/Edge Parameters
Use this sheet to override common parameters for specific nodes or edges.
Leave empty if all nodes/edges should use the common parameters from Demands/Supply/Pipes sheets.
component_type | node_or_edge_id | parameter | value | unit | description
# demand | demand_1 | heatDemand_max | 50000 | W | Individual heat demand for demand_1
# demand | demand_2 | heatDemand_max | 75000 | W | Individual heat demand for demand_2
# pipe | pipe_1_2 | diameter | 0.15 | m | Individual diameter for pipe between node 1 and 2
# pipe | pipe_1_2 | length | 120 | m | Individual length for pipe between node 1 and 2
Instructions:
1. Remove the "#" from example rows to activate them
2. component_type must be: demand, supply, or pipe
3. node_or_edge_id must match IDs in your uesgraph
4. parameter must be a valid parameter name for the template
5. Individual parameters have priority over common parameters