## Assessment Summary
Unit of Assurance — Assessment Summary
Project Name | COU Name | COU Description | Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Assessor Name | Assessment Date | Source Document | Has UQ?
DeltaCool CX-450 Blower CFD Performance Model | CFD prediction of pressure-rise and efficiency curves for CX-450 centrifugal blower used in controller setpoint selection and preliminary fan sizing | Steady RANS CFD model of the CX-450 scroll-type centrifugal blower (Ansys Fluent 2023 R2, k-ω SST, MRF) predicts pressure-rise vs. flow curves and shaft power across 2400–3300 rpm and 0.6–1.15 Qd. Outputs feed building management system commissioning (controller gains, duty points) and procurement shortlisting for electronics cooling skids. No patient or life-safety consequence; downstream lab and site checks provide additional verification. | Complete | N/A | MRL 2 | Medium | ASME-VV40-2018 | Fluids Engineering Group, Thermal Systems Division (independent review: Dr. K. H. Levy) | Date of this assessment (YYYY-MM-DD) | report.md (CFD Credibility Assessment Report — DeltaCool CX-450, prepared by Fluids Engineering Group, Thermal Systems Division, 2026-08-05) | Yes
Legend: |  | Required (Minimal) | Required (Complete) | Optional
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on C3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on I3: [Extract] ¦ Confidence: 50%
Note on K3: [Extract] ¦ Confidence: 50%
Note on L3: [Extract] ¦ Confidence: 50%

## Instructions
UofA Excel Template — Instructions
What is this? | This workbook captures a credibility assessment for one Context of Use (COU). Fill it out, then run `uofa import` to convert it to a machine-verifiable evidence package.
One workbook = one COU | If your project has multiple COUs (e.g., different device classes or risk levels for the same model), create a separate workbook for each.
Profiles | Minimal (7 fields, lightweight audit trail) is for early-stage projects or live pipeline capture. Complete (full V&V 40 assessment) is for regulatory submissions.
Color coding | Blue cells = required for Minimal profile. Green cells = required for Complete profile. White cells = optional.
Credibility Factors | Sheet 4 is pre-populated with all 13 V&V 40 factors from Table 5-1. You do not need to assess all 13 — set Assessed = "No" or "N/A" for factors not relevant to your COU.
Dropdowns | Most constrained fields use dropdown lists. If you need a custom value not in the dropdown, type it directly (the validation will warn but not prevent entry).
After filling out | Run: uofa import your-file.xlsx --sign --key keys/your.key --check
What the tool checks | Gate 1 (SHACL): Are all required fields present? Gate 2 (Jena rules): Are there quality gaps (weakeners)? Gate 3 (Integrity): Is the hash and signature valid?
More info | https://crediblesimulation.com ¦ https://github.com/cloudronin/uofa

## _Lists (hidden)
Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Entity Type | Has UQ | Pass/Fail | Factor Level (1-5) | Factor Status | Decision Outcome | Has UQ (COU-level)
Minimal | Class I | MRL 1 | Low | ASME-VV40-2018 | Requirement | Yes | Pass | 1 | assessed | Accepted | Yes
Complete | Class II | MRL 2 | Medium | NASA-STD-7009B | Model | No | Fail | 2 | not-assessed | Not accepted | No
| Class III | MRL 3 | High | FDA-2023-CMS | Dataset |  | Inconclusive | 3 | scoped-out | Conditional
| Category A | MRL 4 |  | Custom |  |  | N/A | 4 | not-applicable
| Category B | MRL 5 | [5 empty] | 5
Category C
Category D
Category E
Other

## Model & Data
Model & Data — What you modeled and compared against
Entity Type | Name | Identifier / URI | Description | Version | Source
Requirement | Pressure-rise and shaft-power accuracy requirement | Stable URI or local ID | CFD predictions of Δp and shaft power must agree with AMCA 210 test data within ±5% RMS over the validated operating envelope (0.6–1.15 Qd, 2400–3300 rpm, air 20–30°C, sea level) to be accepted for controller setpoint generation and preliminary fan selection | Version number (optional) | Where this came from (optional)
Model | CX-450 steady RANS CFD model |  | Ansys Fluent 2023 R2, incompressible steady RANS, k-ω SST turbulence closure, MRF rotating impeller, poly-hexcore mesh (medium: 8.4M cells, y+≈1), porous inlet screen, surface roughness 1.6 µm Ra
Dataset | AMCA 210 chamber test dataset |  | 42 pressure-rise and shaft-power points at seven speeds (2400–3300 rpm, 150 rpm increments) and six flow points per speed, acquired per AMCA 210 A chamber standard with calibrated instrumentation
Dataset | PIV velocity survey dataset |  | Planar PIV in the mid-height volute at Q=Qd, N=3000 rpm; in-plane velocity uncertainty ±0.08 m/s (k=2); used for local flow-field validation of circumferential angle and velocity magnitude
Dataset | Inlet screen vendor loss-coefficient data sheet |  | Vendor-supplied linear (K) and quadratic (C) porous resistance coefficients for the inlet screen with stated tolerances of ±10% and ±15% respectively
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on A7: [Extract] ¦ Confidence: 50%
Note on B7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%

## Validation Results
Validation Results — What you found when you tested the model
Result Name | Identifier / URI | Description | Compares To | Has UQ? | UQ Method | Metric Value | Pass / Fail
AMCA 210 pressure-rise comparison (42-point matrix) | ValidationResult | What was done, what was found | CFD Δp predictions compared against AMCA 210 A chamber measurements at 42 operating points (seven speeds, six flows each) spanning the full validated envelope | AMCA 210 chamber test data (AFL-2026-027) | Yes | Monte Carlo (200 Latin hypercube samples) propagating numerical, input, and test uncertainties; bootstrapped (1000 resamples) to confirm 95% interval widths | Mean bias +0.4%, RMS error 3.4% of Δp span; largest deviation 6.1% near shutoff; 39/42 points within combined CFD+test 95% confidence bands | Pass
AMCA 210 shaft-power (torque) comparison | ValidationResult |  | CFD shaft-power predictions compared against torque-cell measurements at 42 operating points; positive bias attributed to wall roughness uncertainty and tongue-region separation | AMCA 210 torque measurements (AFL-2026-027) | Yes | Monte Carlo (200 samples); 95% bands ±4.8% typical | RMS error 4.2%; 37/42 points within combined 95% intervals | Pass
PIV local flow-field comparison | ValidationResult |  | Predicted in-plane velocity magnitude and circumferential flow angle compared against planar PIV at Q=Qd, N=3000 rpm in the mid-height volute | PIV survey (PIV-2026-009) | Yes | PIV measurement uncertainty ±0.08 m/s (k=2) reported; CFD uncertainty from mesh and input propagation | Index of agreement 0.91 for velocity magnitude; mean angular deviation 2.8°; localized peak 7° near cutwater | Pass
Mesh convergence and GCI study | ValidationResult |  | Three-level poly-hexcore mesh refinement (3.1M, 8.4M, 21.7M cells) at design point; Richardson extrapolation to estimate discretization error on Δp and torque | Richardson-extrapolated continuum estimate (Δp_extrap = 10.00 kPa) | Yes | Grid Convergence Index (GCI) via Richardson extrapolation; observed order 1.9 | Fine-grid GCI 1.8% on Δp (medium mesh); GCI 2.1% on torque; temporal contribution ≤0.5% | Pass
Code verification — manufactured solution and turbulent flat-plate benchmarks | ValidationResult |  | 2D laminar channel with manufactured-solution body force confirmed second-order accuracy (observed order 2.0 ± 0.1); turbulent flat-plate test confirmed k-ω SST Cf within ±5% of White correlation over Reθ 300–3000 | Analytical manufactured solution; White empirical Cf correlation | No |  | Observed order 2.0 ± 0.1 (channel); Cf within ±5% of White correlation | Pass
Sliding-mesh transient cross-check | ValidationResult |  | Sliding-mesh run at Q=0.9Qd compared time-averaged Δp to steady MRF result to bound temporal modeling error | Steady MRF Δp prediction at Q=0.9Qd | No |  | Δp within 0.5% of MRF; time-step sensitivity (1e-4 vs 5e-5 s) changed Δp by 0.2%; averaging window sensitivity 0.1% | Pass
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on I3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on E4: [Extract] ¦ Confidence: 50%
Note on F4: [Extract] ¦ Confidence: 50%
Note on G4: [Extract] ¦ Confidence: 50%
Note on H4: [Extract] ¦ Confidence: 50%
Note on I4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on G5: [Extract] ¦ Confidence: 50%
Note on H5: [Extract] ¦ Confidence: 50%
Note on I5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on G6: [Extract] ¦ Confidence: 50%
Note on H6: [Extract] ¦ Confidence: 50%
Note on I6: [Extract] ¦ Confidence: 50%
Note on A7: [Extract] ¦ Confidence: 50%
Note on B7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%
Note on E7: [Extract] ¦ Confidence: 50%
Note on F7: [Extract] ¦ Confidence: 50%
Note on H7: [Extract] ¦ Confidence: 50%
Note on I7: [Extract] ¦ Confidence: 50%
Note on A8: [Extract] ¦ Confidence: 50%
Note on B8: [Extract] ¦ Confidence: 50%
Note on D8: [Extract] ¦ Confidence: 50%
Note on E8: [Extract] ¦ Confidence: 50%
Note on F8: [Extract] ¦ Confidence: 50%
Note on H8: [Extract] ¦ Confidence: 50%
Note on I8: [Extract] ¦ Confidence: 50%

## Credibility Factors
Credibility Factors — V&V 40 Table 5-1 Assessment
Complete profile only. Assess each relevant factor: set Required Level (goal given model risk) and Achieved Level (what evidence supports).
Factor Type | Category | Required Level | Achieved Level | Acceptance Criteria | Rationale | Factor Status | Linked Evidence
V&V 40 factor (pre-filled, do not edit) | Grouping (pre-filled) | Credibility goal for this factor (1-5) | Level achieved by evidence (1-5) | Goal and basis for the required level (from V&V 40 Tables 3-4) | Brief justification (esp. if achieved < required) | assessed / not-assessed / scoped-out / not-applicable | URI of validation result that supports this factor (optional)
Software quality assurance | Verification — Code | 2 | 4 | Software is a validated commercial solver with documented QA processes and version control | Ansys Fluent 2023 R2 is a commercial solver used in double-precision mode. Cases are tracked in Git (tag v1.3.2) with mesh and BC file hashes logged in a results manifest. Automated CI regression tests run two canonical cases (Poiseuille, turbulent flat plate) with tolerance bands before release. Pre-run sanity checks (mesh quality, negative-volume detection, boundary-unit consistency) are enforced by CI. Containerized execution environment pins OS libraries. HPC repeatability confirmed: Δp within 0.1%, torque within 0.2% across independent runs. Repository structure includes cases, scripts, post-processing notebooks, and CI definitions (appendix.md A7). | assessed
Numerical code verification | Verification — Code | 2 | 4 | Solver correctly reproduces known solutions for relevant equation types | Two standard benchmark problems executed: (1) 2D laminar channel with manufactured-solution body force yielded observed spatial order 2.0 ± 0.1, consistent with second-order schemes; (2) turbulent flat-plate over Reθ 300–3000 matched White Cf correlation within ±5% using identical k-ω SST settings as production. These checks reduce risk of silent numerical defects in the toolchain (report.md Section 5). | assessed
Discretization error | Verification — Calculation | 3 | 4 | Mesh-induced error on primary QoI (Δp) is quantified and within acceptable bounds relative to the ±5% accuracy target | Three-level poly-hexcore refinement (3.1M, 8.4M, 21.7M cells) at design condition. Δp values: 9.72, 9.89, 9.96 kPa. Richardson extrapolation with observed order 1.9 gives fine-grid GCI 1.8% on Δp and 2.1% on torque for the medium production mesh. Temporal sensitivity (sliding mesh): time-step change 0.2%, averaging window 0.1%. Both are well within the ±5% accuracy target. Mesh quality documented: 95th-percentile skewness 0.28, minimum orthogonal quality 0.13 (appendix.md A1, A3; report.md Section 4). | assessed
Numerical solver error | Verification — Calculation | 2 | 4 | Iterative convergence is demonstrated to be adequate so solver errors are negligible relative to discretization and modeling uncertainties | Residual targets: continuity and momentum below 1e-5; k and ω below 1e-6. Integral monitors (Δp and torque) stabilized within 0.2% drift over the final 500 iterations at the design point. Residuals fell below 1e-5 by 1100 iterations; Δp plateaued after 900 iterations. MRF rotating frame ramped over 300 iterations to mitigate transients. Pressure-based coupled algorithm with second-order spatial schemes used throughout (appendix.md A2; report.md Sections 3–4). | assessed
Use error | Verification — Calculation | 2 | 4 | Model setup is independently reviewed and confirmed correct; boundary conditions and geometry are traceable | Independent review by Dr. K. H. Levy (senior CFD specialist, unrelated product line) confirmed mesh strategy and solver settings are consistent with published best practices for scroll blowers. Reviewer requests (transient spot-check, explicit porous coefficient documentation) were resolved before report finalization; closure committed under PR #118 with before/after plots (appendix.md A8; report.md Section 15). Runbook checklist in repository; single-click script regenerates all plots and metrics. Case IDs, solver version, mesh ID, and post-processing script hashes stored per case. AMCA 210 A chamber geometry included in model to avoid pressure-datum ambiguity. | assessed
Model form | Validation — Model | 2 | 3 | Governing equations and turbulence closure are justified for the flow regime and intended outputs | Incompressible isothermal steady RANS justified by maximum Mach number <0.18 at impeller exit; compressibility correction tested and changed Δp by <0.3%. k-ω SST chosen over realizable k-ε because SST showed better conformity with PIV near the tongue (up to 3.5% vs 1.8% deviation at near-shutoff). Frozen-rotor MRF validated against sliding mesh (Δp within 0.5%). Low-Re near-wall treatment with y+<1. Out-of-scope physics (acoustics, surge, condensation) explicitly documented. Known limitation at near-shutoff (recirculation increases error to ~6%) is acknowledged and trimmed from the approved envelope (report.md Sections 2, 10, 17). | assessed
Model inputs | Validation — Model | 2 | 4 | Boundary conditions and material properties are grounded in measurement or vetted vendor data with characterized uncertainties | Inlet total pressure from calibrated nozzle; turbulence intensity 2.5% ± 0.5% from hotwire survey. Speed set per RPM boundary. Air properties at 25°C used (density 1.184 kg/m³, viscosity 1.849e-5 Pa·s). Porous screen K and C from vendor data sheet (VS-IX-450 Rev B) with ±10% and ±15% tolerances; one permitted within-tolerance adjustment (K+5%, C-7%) at a single shakedown point, transparently documented. Wall roughness 1.6 µm Ra from drawing; mapped to sand-grain roughness. All inputs have certificates or data sheets in records folder. Sensitivity screening (Morris method) identified K and C as dominant inputs (normalized elementary effects 2.1 and 1.6); turbulence intensity and roughness also bounded (appendix.md A6; report.md Sections 6–7, 10). | assessed
Test samples | Validation — Comparator | 2 | 3 | Experimental data are representative of the production device and sufficient in quantity to characterize performance across the COU envelope | 42 test points across seven speeds (2400–3300 rpm, 150 rpm increments) and six flow rates per speed, spanning the full validated envelope. Single physical test article (CX-450 blower) in an AMCA 210 A chamber. Test-to-test repeatability within ±0.5% at fixed setpoints. PIV survey conducted at a single condition (Qd, 3000 rpm). No statistical characterization of multiple production units; sample size is one physical device, which is typical for industrial blower performance studies but limits statistical generalizability to unit-to-unit variability (report.md Sections 8–9). | assessed
Test conditions | Validation — Comparator | 2 | 4 | Test conditions are well-controlled, traceable to calibrated standards, and measurement uncertainties are quantified | AMCA 210 A chamber with calibrated instrumentation: differential pressure transducers ±0.25% FS, torque cell ±0.3% FS, tachometer ±0.05% FS, ambient T/P ±0.2°C/±0.5 kPa. Flow via nozzle method, ISO 5167 orifice plate calibration; combined volumetric flow uncertainty ±0.9% (k=2). PIV in-plane velocity uncertainty ±0.08 m/s (k=2). AMCA kinetic-energy chamber correction applied. Test temperature and pressure matched modeling assumptions within specified ± range. All instrumentation referenced to national standards via calibration chain (report.md Section 8). | assessed
Equivalency of input parameters | Validation — Assessment | 2 | 3 | CFD boundary conditions match the experimental test conditions with documented correspondence and uncertainty propagation | AMCA 210 A chamber geometry included in the CFD model to align pressure datum; inlet total pressure derived from the same calibrated nozzle used in tests; turbulence intensity matched to hotwire measurement (2.5% ± 0.5%); speed, temperature, and ambient pressure conditions matched within stated ranges. Porous screen coefficients from the same vendor data sheet as the physical unit. One within-tolerance parameter adjustment documented. Monte Carlo propagation combined numerical, input, and test uncertainties into a unified 95% band to assess net correspondence. Environmental match (temperature, sea-level pressure) confirmed within test tolerances (report.md Sections 6, 9, 11). | assessed
Output comparison | Validation — Assessment | 3 | 4 | Quantitative comparison metrics demonstrate model predictions meet ±5% accuracy target for Δp and shaft power across the validated envelope; uncertainty bands are reported | Pressure rise: mean bias +0.4%, RMS error 3.4% over 42 points (within ±5% target); largest deviation 6.1% near shutoff (outside approved domain). Shaft power: RMS error 4.2%, positive bias noted. PIV: index of agreement 0.91 for velocity magnitude, mean angular deviation 2.8° (peak 7° at cutwater). Coverage: 39/42 AMCA Δp points and 37/42 torque points within combined CFD+test 95% intervals. Uncertainty bands: Monte Carlo 95% bands ±4.1% (Δp at Qd) to ±5.2% (near shutoff). Both bulk (AMCA) and local (PIV) comparisons provided. Prior fan families (BX-320, DX-510) showed RMS 3.1% and 3.7%, consistent with present results (report.md Sections 9, 11, 14). | assessed
Relevance of the quantities of interest | Applicability | 2 | 4 | Model outputs (Δp, shaft power) directly address the engineering decision (controller setpoint selection, fan sizing) and are measurable both computationally and experimentally | The primary QoIs are pressure rise (Δp) and shaft power, which directly feed controller gain setting and duty-point definition in the BMS commissioning plan, and procurement shortlisting. Both QoIs are computed by the CFD model and measured by the AMCA 210 A chamber (Δp via transducers, power via torque cell and tachometer). Local velocity field from PIV provides a secondary QoI confirming internal flow structure. The connection between CFD output and the engineering decision is explicitly stated; a ±5% accuracy band is defined as fit-for-purpose for the commissioning use (report.md Sections 1, 16). | assessed
Relevance of the validation activities to the COU | Applicability | 3 | 3 | Validation conditions span the full COU operating envelope and use the same geometry, fluid, and physics regime as the intended application | Validation covers the full speed range (2400–3300 rpm) and flow range tested (0.55–1.2 Qd), with approved envelope trimmed to 0.6–1.15 Qd where agreement is good. Working fluid (air, 20–30°C, sea level) matches COU. Geometry is the production CX-450 casing and impeller with the AMCA 210 A chamber. Gaps acknowledged: (1) near-shutoff recirculation regime is outside approved domain; (2) no multi-unit statistical coverage; (3) altitude above 1500 m not validated; (4) thermal and acoustic physics not covered; (5) PIV covers only one operating point. The approved COU envelope is explicitly bounded to match what is validated; extrapolation rules are documented (report.md Sections 9, 12, 17; appendix.md A9). | assessed
Note on C5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on G5: [Extract] ¦ Confidence: 50%
Note on C6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on G6: [Extract] ¦ Confidence: 50%
Note on C7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%
Note on E7: [Extract] ¦ Confidence: 50%
Note on F7: [Extract] ¦ Confidence: 50%
Note on G7: [Extract] ¦ Confidence: 50%
Note on C8: [Extract] ¦ Confidence: 50%
Note on D8: [Extract] ¦ Confidence: 50%
Note on E8: [Extract] ¦ Confidence: 50%
Note on F8: [Extract] ¦ Confidence: 50%
Note on G8: [Extract] ¦ Confidence: 50%
Note on C9: [Extract] ¦ Confidence: 50%
Note on D9: [Extract] ¦ Confidence: 50%
Note on E9: [Extract] ¦ Confidence: 50%
Note on F9: [Extract] ¦ Confidence: 50%
Note on G9: [Extract] ¦ Confidence: 50%
Note on C10: [Extract] ¦ Confidence: 50%
Note on D10: [Extract] ¦ Confidence: 50%
Note on E10: [Extract] ¦ Confidence: 50%
Note on F10: [Extract] ¦ Confidence: 50%
Note on G10: [Extract] ¦ Confidence: 50%
Note on C11: [Extract] ¦ Confidence: 50%
Note on D11: [Extract] ¦ Confidence: 50%
Note on E11: [Extract] ¦ Confidence: 50%
Note on F11: [Extract] ¦ Confidence: 50%
Note on G11: [Extract] ¦ Confidence: 50%
Note on C12: [Extract] ¦ Confidence: 50%
Note on D12: [Extract] ¦ Confidence: 50%
Note on E12: [Extract] ¦ Confidence: 50%
Note on F12: [Extract] ¦ Confidence: 50%
Note on G12: [Extract] ¦ Confidence: 50%
Note on C13: [Extract] ¦ Confidence: 50%
Note on D13: [Extract] ¦ Confidence: 50%
Note on E13: [Extract] ¦ Confidence: 50%
Note on F13: [Extract] ¦ Confidence: 50%
Note on G13: [Extract] ¦ Confidence: 50%
Note on C14: [Extract] ¦ Confidence: 50%
Note on D14: [Extract] ¦ Confidence: 50%
Note on E14: [Extract] ¦ Confidence: 50%
Note on F14: [Extract] ¦ Confidence: 50%
Note on G14: [Extract] ¦ Confidence: 50%
Note on C15: [Extract] ¦ Confidence: 50%
Note on D15: [Extract] ¦ Confidence: 50%
Note on E15: [Extract] ¦ Confidence: 50%
Note on F15: [Extract] ¦ Confidence: 50%
Note on G15: [Extract] ¦ Confidence: 50%
Note on C16: [Extract] ¦ Confidence: 50%
Note on D16: [Extract] ¦ Confidence: 50%
Note on E16: [Extract] ¦ Confidence: 50%
Note on F16: [Extract] ¦ Confidence: 50%
Note on G16: [Extract] ¦ Confidence: 50%
Note on C17: [Extract] ¦ Confidence: 50%
Note on D17: [Extract] ¦ Confidence: 50%
Note on E17: [Extract] ¦ Confidence: 50%
Note on F17: [Extract] ¦ Confidence: 50%
Note on G17: [Extract] ¦ Confidence: 50%

## Decision
Decision — The credibility judgment
Decision Outcome | Decision Rationale | Criteria Set | Decided By | Decision Date
Accepted | The CFD model achieves RMS Δp error of 3.4% and shaft-power RMS error of 4.2% against 42 AMCA 210 test points, both within the stated ±5% fit-for-purpose accuracy target. 39/42 Δp points and 37/42 torque points fall within combined 95% uncertainty bands. PIV index of agreement is 0.91. Mesh GCI is 1.8% on Δp; code verification benchmarks confirm second-order accuracy. Independent specialist review (Dr. K. H. Levy) was completed and all findings resolved. Model is accepted for controller setpoint generation and preliminary fan selection for the CX-450 within the validated envelope (air 20–30°C, 0.6–1.15 Qd, 2400–3300 rpm) subject to use of Ansys Fluent 2023 R2 with k-ω SST, poly-hexcore mesh at or finer than the medium density (8.4M cells, y+≈1), the documented runbook and version-controlled scripts, and a commissioning lab cross-check of 2–3 mid-to-high-flow points with pause-and-notify if deviations exceed ±5%. Not approved for acoustics, surge/deep off-design, altitudes above 1500 m, or other impeller trims without re-assessment. | Auto-filled from Assessment Summary | M. M. Raines (Head of Thermal Systems) upon recommendation of Fluids Engineering Group and review sign-off by Dr. K. H. Levy | 2026-08-05
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%