## Assessment Summary
Unit of Assurance — Assessment Summary
Project Name | COU Name | COU Description | Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Assessor Name | Assessment Date | Source Document | Has UQ?
Cleanroom Supply Diffuser CFD Study | Rank diffuser layout options and estimate zone-average downflow velocity in a Grade B cleanroom bay | CFD model of a 10.6 m × 5.2 m × 3.0 m Grade B cleanroom bay with five ceiling-mounted perforated diffusers. Used to rank layout options for recovery time and velocity uniformity over a 1.2 m × 2.4 m work zone, and to gauge whether average downflow at 1.0 m above floor meets 0.45 m/s ± 20% guidance. Not used for ISO-14644 compliance demonstration or local velocity prediction near returns or racks. | Complete | N/A | MRL 3 | Medium | ASME-VV40-2018 | M. Jernigan (CFD); S. Patel (Test); L. Ortega (CCB Chair) | Date of this assessment (YYYY-MM-DD) | report.md (CFD Credibility Slide Deck — Cleanroom Supply Diffuser Study, vv40-aligned; contacts: M. Jernigan, S. Patel, CCB Chair L. Ortega) | Yes
Legend: |  | Required (Minimal) | Required (Complete) | Optional
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on C3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on I3: [Extract] ¦ Confidence: 50%
Note on K3: [Extract] ¦ Confidence: 50%
Note on L3: [Extract] ¦ Confidence: 50%

## Instructions
UofA Excel Template — Instructions
What is this? | This workbook captures a credibility assessment for one Context of Use (COU). Fill it out, then run `uofa import` to convert it to a machine-verifiable evidence package.
One workbook = one COU | If your project has multiple COUs (e.g., different device classes or risk levels for the same model), create a separate workbook for each.
Profiles | Minimal (7 fields, lightweight audit trail) is for early-stage projects or live pipeline capture. Complete (full V&V 40 assessment) is for regulatory submissions.
Color coding | Blue cells = required for Minimal profile. Green cells = required for Complete profile. White cells = optional.
Credibility Factors | Sheet 4 is pre-populated with all 13 V&V 40 factors from Table 5-1. You do not need to assess all 13 — set Assessed = "No" or "N/A" for factors not relevant to your COU.
Dropdowns | Most constrained fields use dropdown lists. If you need a custom value not in the dropdown, type it directly (the validation will warn but not prevent entry).
After filling out | Run: uofa import your-file.xlsx --sign --key keys/your.key --check
What the tool checks | Gate 1 (SHACL): Are all required fields present? Gate 2 (Jena rules): Are there quality gaps (weakeners)? Gate 3 (Integrity): Is the hash and signature valid?
More info | https://crediblesimulation.com ¦ https://github.com/cloudronin/uofa

## _Lists (hidden)
Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Entity Type | Has UQ | Pass/Fail | Factor Level (1-5) | Factor Status | Decision Outcome | Has UQ (COU-level)
Minimal | Class I | MRL 1 | Low | ASME-VV40-2018 | Requirement | Yes | Pass | 1 | assessed | Accepted | Yes
Complete | Class II | MRL 2 | Medium | NASA-STD-7009B | Model | No | Fail | 2 | not-assessed | Not accepted | No
| Class III | MRL 3 | High | FDA-2023-CMS | Dataset |  | Inconclusive | 3 | scoped-out | Conditional
| Category A | MRL 4 |  | Custom |  |  | N/A | 4 | not-applicable
| Category B | MRL 5 | [5 empty] | 5
Category C
Category D
Category E
Other

## Model & Data
Model & Data — What you modeled and compared against
Entity Type | Name | Identifier / URI | Description | Version | Source
Requirement | Zone-average downflow velocity requirement | Stable URI or local ID | Zone-average downflow velocity at 1.0 m above floor must meet 0.45 m/s ± 20% guidance for the 1.2 m × 2.4 m work zone; model accepted for layout ranking and rough-order velocity estimates only, not for ISO-14644 compliance or local velocity prediction within 0.1 m/s near returns or racks. | Version number (optional) | Where this came from (optional)
Model | Ansys Fluent 2023 R2 CFD Model — Cleanroom Bay |  | Steady-state, incompressible RANS CFD model of cleanroom bay using realizable k-ε with scalable wall functions; hex-dominant unstructured mesh at three refinement levels (1.2M, 3.8M, 7.5M cells); diffusers modeled as uniform porous jumps; racks as porous blocks.
Dataset | Full-Scale Mockup Hot-Wire Anemometry Dataset |  | 16-probe hot-wire anemometer grid at 1.0 m height in full-scale mockup bay; 60 s averages per probe; flow-bench-certified diffusers at 0.204 kg/s ± 2%; repeatability std dev ~0.02 m/s. Includes ambient temperature anomaly (24–25°C) in first two runs and one diffuser grille swap to 48% OA variant in test 3.
Dataset | LHS Uncertainty Quantification Sample Set |  | Latin Hypercube Sampling across four inputs (supply split, return static pressure, rack porous resistance, diffuser loss coefficient); 300 draws planned; 28 runs post-processed after queue failures and convergence filtering; 95% velocity band 0.39–0.53 m/s reported.
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%

## Validation Results
Validation Results — What you found when you tested the model
Result Name | Identifier / URI | Description | Compares To | Has UQ? | UQ Method | Metric Value | Pass / Fail
CFD vs. Hot-Wire Anemometry Velocity Comparison | ValidationResult | What was done, what was found | Zone-average velocity and probe-by-probe velocity at 1.0 m height compared between CFD (realizable k-ε, 3.8M–7.5M mesh) and full-scale mockup hot-wire measurements at 16 locations. Two reporting roll-ups exist: 6% MAE excluding two suspect probes (P2, P13), and 11.8% MAE including all probes; 88% vs. 75% of probes within ±20% of mean respectively. | Full-scale mockup hot-wire anemometry dataset (LabBook_CRBAY_May2026_pages_14–23) | Yes | Latin Hypercube Sampling (28 runs post-processed); 95% band reported | MAE 6% (16 probes, 2 excluded) / MAE 11.8% (all 16 probes); 88% / 75% of probes within ±20% | Inconclusive
Mesh Convergence Study | ValidationResult |  | Three mesh levels (1.2M, 3.8M, 7.5M cells) compared at 12 probe points at 1.0 m height. Velocity at probe P7 changed 3.1% from 3.8M to 7.5M; P3 changed -0.4%. Non-monotone trend observed at P11 (1.2M: 0.47, 3.8M: 0.43, 7.5M: 0.45 m/s). No formal GCI computed. | Coarser mesh solutions (internal convergence) | No |  | 3.1% max velocity change from 3.8M to 7.5M; non-monotone at P11 | Inconclusive
Canonical Code Verification Cases | ValidationResult |  | Laminar Poiseuille flow and backward-facing step used as sanity checks on Ansys Fluent 2023 R2. Poiseuille velocity yielded ~1.9 order of convergence on grid halving. Qualitative expected trends confirmed for backward-facing step. | Analytical solution (Poiseuille); expected trends (backward-facing step) | No |  | ~1.9 observed order of convergence (Poiseuille velocity) | Pass
Iterative Convergence Monitoring | ValidationResult |  | 12 monitor probes at 1.0 m height tracked over iterations. Final runs used relaxed momentum residual target of 1e-4 (target was 1e-5); probes plateaued to <0.3% drift over last 500 iterations. Two runs restarted with different under-relaxation factors to achieve overnight closure. | Residual and probe drift targets | No |  | <0.3% probe drift over last 500 iterations; momentum residual relaxed to 1e-4 | Inconclusive
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on I3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on E4: [Extract] ¦ Confidence: 50%
Note on F4: [Extract] ¦ Confidence: 50%
Note on H4: [Extract] ¦ Confidence: 50%
Note on I4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on H5: [Extract] ¦ Confidence: 50%
Note on I5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on H6: [Extract] ¦ Confidence: 50%
Note on I6: [Extract] ¦ Confidence: 50%

## Credibility Factors
Credibility Factors — V&V 40 Table 5-1 Assessment
Complete profile only. Assess each relevant factor: set Required Level (goal given model risk) and Achieved Level (what evidence supports).
Factor Type | Category | Required Level | Achieved Level | Acceptance Criteria | Rationale | Factor Status | Linked Evidence
V&V 40 factor (pre-filled, do not edit) | Grouping (pre-filled) | Credibility goal for this factor (1-5) | Level achieved by evidence (1-5) | Goal and basis for the required level (from V&V 40 Tables 3-4) | Brief justification (esp. if achieved < required) | assessed / not-assessed / scoped-out / not-applicable | URI of validation result that supports this factor (optional)
Software quality assurance | Verification — Code | 3 | 3 | Commercial solver with documented version control, patch management, and basic regression evidence | Ansys Fluent 2023 R2 (commercial solver) used in double-precision mode. GitLab version control with tags v1.3–v1.7 documented. One hotfix (HF-2023R2-19) applied mid-campaign with partial change-log review. Python post-processing scripts unit-tested; a units mismatch bug corrected after first five runs. No formal ISO quality process or external certification audit cited, but commercial solver with version tracking and scripted post-processing constitutes adequate evidence for MRL 3. | assessed
Numerical code verification | Verification — Code | 3 | 2 | Code correctly reproduces known analytical or benchmark solutions with demonstrated convergence order | Laminar Poiseuille flow showed ~1.9 order of convergence on grid halving (close to expected second order). Backward-facing step yielded expected qualitative trends only — no quantitative error metric reported. Coverage is limited to two simple cases; no MMS or published benchmark with quantified error norms. Adequate for basic confidence but falls short of thorough verification. | assessed
Discretization error | Verification — Calculation | 3 | 2 | Mesh convergence demonstrated with quantified error or GCI across refinement levels for primary QoI | Three mesh levels (1.2M, 3.8M, 7.5M) studied; max velocity change 3.1% from medium to fine at P7. Non-monotone behavior at P11 undermines Richardson extrapolation. No GCI computed. Production runs used realizable k-ε with wall functions at y+ 28–45, inconsistent with stated y+ < 1 target. Spatial discretization order switched from QUICK (scoping) to first-order upwind (final) without re-verifying grid sensitivity. Basic evidence with notable gaps. | assessed
Numerical solver error | Verification — Calculation | 3 | 2 | Residual convergence and probe monitor plateau documented for all production runs | Target residuals 1e-5 (momentum) and 1e-6 (continuity) specified; momentum target relaxed to 1e-4 for final batch to achieve closure. Probe monitors plateaued to <0.3% drift over last 500 iterations — positive evidence. Two runs restarted with altered under-relaxation. Coupled scheme residual norm behavior changed after HF-2023R2-19 patch. Relaxed residual targets and restart variability reduce confidence, though probe plateau partially compensates. | assessed
Use error | Verification — Calculation | 3 | 2 | Independent review of boundary conditions, geometry setup, and post-processing confirmed; no critical setup errors remaining | Internal peer review by two CFD practitioners conducted; no external audit. A units mismatch (Pa vs inH2O) in return pressure logging was found and corrected after five runs — indicating a setup error that affected early results. Operating point ambiguity (1.20 vs. 1.00 kg/s in case labels vs. output files) not fully resolved at time of assessment. Numerics switched (QUICK to first-order, SST to k-ε) without full re-check. Peer review present but setup errors and ambiguities indicate basic-level use error control. | assessed
Model form | Validation — Model | 3 | 2 | Governing equations and turbulence model selection justified with documented limitations; known physics gaps identified | Steady RANS with realizable k-ε and scalable wall functions used for production; SST k-ω used only for scoping. Constant-density assumption justified by weak ΔT (<2 K). Known model-form gaps documented: door leakage omitted, returns idealized, no filter media resistance, buoyancy not modeled for heated racks. Turbulence model switch from SST to k-ε not validated with near-return profiles; over-smoothing of recirculation near returns acknowledged. Limitations documented but turbulence model selection rationale is incomplete and not validated at the switch. | assessed
Model inputs | Validation — Model | 3 | 2 | Key boundary conditions and material properties characterized with uncertainty; geometry consistent with test article | Diffuser loss coefficient provided by vendor (AeroClean) curve only — no raw bench data shared. Inlet turbulence intensity assumed at 5%; AHU spec suggests 1–2% downstream of HEPA, creating an unresolved discrepancy. Supply flow rate ambiguity (1.20 vs. 1.00 kg/s) between CFD setup and test not resolved. CAD indicates 9 mm plenum height difference at two locations versus test article. One test diffuser swapped to 48% OA variant not reflected in model geometry. Input uncertainty partially characterized via LHS but diffuser coefficient treated as random rather than epistemic. | assessed
Test samples | Validation — Comparator | 2 | 3 | Test article representative of modeled geometry; diffusers characterized; adequate number of measurement locations | Full-scale mockup bay used with same diffuser model (AeroClean ACF-24, 45% OA perforated plate). Diffusers flow-bench certified at 0.204 kg/s ± 2% per unit. 16 probe locations in work zone with 60 s averages and documented repeatability (std dev ~0.02 m/s). One grille replaced with 48% OA variant during test 3 introduces a deviation. Ambient temperature anomaly (24–25°C) in first two runs noted. Overall a genuine full-scale test article with reasonable characterization. | assessed
Test conditions | Validation — Comparator | 2 | 2 | Test conditions measured and controlled; instrumentation calibrated; environmental conditions documented | Room held at neutral buoyancy, nominal 20°C, 101 kPa for most runs. Calibrated hot-wire anemometers with documented repeatability. However, first two runs conducted at 24–25°C due to AHU recalibration — a controlled-condition failure not fully corrected in the comparison dataset. Blower setpoint gave 1.00 kg/s on rotameter versus 1.20 kg/s nominal. Test logbook (LabBook_CRBAY_May2026) provides traceability. Measurement uncertainty quantified only for repeatability; calibration uncertainty not reported. Basic evidence with condition control gaps. | assessed
Equivalency of input parameters | Validation — Assessment | 3 | 1 | CFD boundary conditions demonstrably match experimental conditions within stated tolerances for all primary inputs | Significant unresolved mismatch between CFD and test: operating flow rate 1.20 kg/s (CFD nominal/label) vs. 1.00 kg/s (test rotameter and CFD output file integral). Turbulence intensity assumed 5% in CFD vs. 1–2% measured downstream of HEPA. Ambient temperature 20°C in CFD vs. 24–25°C in first two test runs. Plenum geometry differs by 9 mm at two locations. One diffuser grille variant (48% OA) in test not matched in model. These are multiple simultaneous unresolved input mismatches affecting the primary QoI, constituting minimal equivalency. | assessed
Output comparison | Validation — Assessment | 3 | 2 | Quantitative error metrics reported for all probes; uncertainty bands cover test data; consistent reporting of outlier handling | Quantitative comparison at 16 probes reported with MAE and proportion within ±20% band. However, two conflicting roll-ups exist (6% MAE excluding P2/P13 vs. 11.8% including all probes) without defensible instrument error analysis to justify exclusion. UQ coverage claimed as >90% but engineering log recalculation shows only 72% of probe readings within the propagated band. Bias identified under strong return suction. Secondary QoI (recovery time) not validated. Partial quantitative comparison with significant reporting inconsistencies. | assessed
Relevance of the quantities of interest | Applicability | 3 | 3 | QoI (zone-average velocity, uniformity index) directly measurable both in CFD and experiment and relevant to the layout selection decision | Primary QoI is zone-average velocity at 1.0 m and uniformity index (std dev/mean) — both directly measurable in CFD (12–16 probe points) and experiment (16 hot-wire probes at same height). These QoIs directly relate to the decision of diffuser layout selection and the 0.45 m/s ± 20% guidance. Recovery time identified as a QoI but not validated (no transient test conducted). Core QoIs are well-defined and measurable in both domains. | assessed
Relevance of the validation activities to the COU | Applicability | 3 | 2 | Validation conditions (geometry, flow rates, diffuser type, room size) match the intended COU operating envelope | Full-scale mockup of same bay dimensions and same diffuser model (ACF-24) used — strong geometric relevance. However, operating point mismatch (1.00 vs. 1.20 kg/s) means validation was not conducted at the COU nominal flow. Heated-rack scenarios (Phase 2 COU) not covered. Door leakage and transient events not tested. Sensitivity screening on 3.8M mesh without SST k-ω check limits turbulence model applicability near returns. Validation covers the core steady-state layout ranking scenario adequately but with operating condition gaps that limit direct applicability. | assessed
Note on C5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on G5: [Extract] ¦ Confidence: 50%
Note on C6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on G6: [Extract] ¦ Confidence: 50%
Note on C7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%
Note on E7: [Extract] ¦ Confidence: 50%
Note on F7: [Extract] ¦ Confidence: 50%
Note on G7: [Extract] ¦ Confidence: 50%
Note on C8: [Extract] ¦ Confidence: 50%
Note on D8: [Extract] ¦ Confidence: 50%
Note on E8: [Extract] ¦ Confidence: 50%
Note on F8: [Extract] ¦ Confidence: 50%
Note on G8: [Extract] ¦ Confidence: 50%
Note on C9: [Extract] ¦ Confidence: 50%
Note on D9: [Extract] ¦ Confidence: 50%
Note on E9: [Extract] ¦ Confidence: 50%
Note on F9: [Extract] ¦ Confidence: 50%
Note on G9: [Extract] ¦ Confidence: 50%
Note on C10: [Extract] ¦ Confidence: 50%
Note on D10: [Extract] ¦ Confidence: 50%
Note on E10: [Extract] ¦ Confidence: 50%
Note on F10: [Extract] ¦ Confidence: 50%
Note on G10: [Extract] ¦ Confidence: 50%
Note on C11: [Extract] ¦ Confidence: 50%
Note on D11: [Extract] ¦ Confidence: 50%
Note on E11: [Extract] ¦ Confidence: 50%
Note on F11: [Extract] ¦ Confidence: 50%
Note on G11: [Extract] ¦ Confidence: 50%
Note on C12: [Extract] ¦ Confidence: 50%
Note on D12: [Extract] ¦ Confidence: 50%
Note on E12: [Extract] ¦ Confidence: 50%
Note on F12: [Extract] ¦ Confidence: 50%
Note on G12: [Extract] ¦ Confidence: 50%
Note on C13: [Extract] ¦ Confidence: 50%
Note on D13: [Extract] ¦ Confidence: 50%
Note on E13: [Extract] ¦ Confidence: 50%
Note on F13: [Extract] ¦ Confidence: 50%
Note on G13: [Extract] ¦ Confidence: 50%
Note on C14: [Extract] ¦ Confidence: 50%
Note on D14: [Extract] ¦ Confidence: 50%
Note on E14: [Extract] ¦ Confidence: 50%
Note on F14: [Extract] ¦ Confidence: 50%
Note on G14: [Extract] ¦ Confidence: 50%
Note on C15: [Extract] ¦ Confidence: 50%
Note on D15: [Extract] ¦ Confidence: 50%
Note on E15: [Extract] ¦ Confidence: 50%
Note on F15: [Extract] ¦ Confidence: 50%
Note on G15: [Extract] ¦ Confidence: 50%
Note on C16: [Extract] ¦ Confidence: 50%
Note on D16: [Extract] ¦ Confidence: 50%
Note on E16: [Extract] ¦ Confidence: 50%
Note on F16: [Extract] ¦ Confidence: 50%
Note on G16: [Extract] ¦ Confidence: 50%
Note on C17: [Extract] ¦ Confidence: 50%
Note on D17: [Extract] ¦ Confidence: 50%
Note on E17: [Extract] ¦ Confidence: 50%
Note on F17: [Extract] ¦ Confidence: 50%
Note on G17: [Extract] ¦ Confidence: 50%

## Decision
Decision — The credibility judgment
Decision Outcome | Decision Rationale | Criteria Set | Decided By | Decision Date
Accepted | The Cleanroom Upgrade CCB accepted the CFD model on 2026-08-05 for the specific purpose of ranking diffuser layouts and providing rough-order estimates of zone-average velocity in the specified Grade B cleanroom bay. Acceptance is conditioned on: (1) use of realizable k-ε with documented wall-function setup and mesh ≥3.8M cells; (2) matching blower mass flow in CFD within ±2% of as-tested value with documentation in the case header; (3) reporting both the 6% and 11.8% MAE figures with explicit probe inclusion criteria; and (4) not using the current UQ coverage claim until at least 100 LHS samples are rerun. The model is explicitly not accepted for ISO-14644 compliance demonstration or for predicting local velocities within 0.1 m/s near returns or racks. Key concerns driving conditions include unresolved operating point mismatch (1.20 vs. 1.00 kg/s), overstated UQ coverage (claimed >90%, recalculated 72%), inconsistent outlier handling in validation roll-up, and turbulence model switch without re-verification near returns. | Auto-filled from Assessment Summary | L. Ortega (CCB Chair) | 2026-08-05
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%